## CoverSheet
EDB Information Disclosure Requirements
Information Templates
for
Schedules 1–10
| Company Name | Alpine Energy Limitied
| Disclosure Date | 2014-08-31
| Disclosure Year (year ended) | 2014-03-31
Templates for Schedules 1–10
Template Version 3.0. Prepared 14 April 2014

## TOC
Table of Contents
Schedule | Description
1 | Analytical Ratios
2 | Report on Return on Investment
3 | Report on Regulatory Profit
4 | Report on Value of the Regulatory Asset Base (Rolled Forward)
5a | Report on Regulatory Tax Allowance
5b | Report on Related Party Transactions
5c | Report on Term Credit Spread Differential Allowance
5d | Report on Cost Allocations
5e | Report on Asset Allocations
6a | Report on Capital Expenditure for the Disclosure Year
6b | Report on Operational Expenditure for the Disclosure Year
7 | Comparison of Forecasts to Actual Expenditure
8 | Report on Billed Quantities and Line Charge Revenues (by Price Component)
9a | Asset Register
9b | Asset Age Profile
9c | Report on Overhead Lines
9d | Report on Embedded Networks
9e | Report on Demand
10 | Report on Network Reliability

## Guidelines
Disclosure Template Guidelines for Information Entry
These templates have been prepared for use by EDBs when making disclosures under subclauses 2.3.1, 2.4.21, 2.4.22, 2.5.1, and 2.5.2 of the Electricity Distribution Information Disclosure Determination 2012. Disclosures must be made available to the public within 5 months after the end of the disclosure year and a copy provided to the Commission within 5 working days of being disclosed to the public.
Version 3.0 templates
These templates correct formula errors contained in previous versions of the templates. A list of the formula corrections can be found in the ID issues register under "Excel Template Issues - v2.X (2013)" in the category column. We have included additional guidance for schedules 2, 4 and 5a indicating where information for certain rows are expected to be sourced from.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2013").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell. Under no circumstances should the formulas in a calculated cell be overwritten.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Conditional Formatting Settings on Data Entry Cells
Schedule 9b columns AA to AE (2013 to 2017) contain conditional formatting. The data entry cells for future years are hidden (are changed from white to yellow). Schedule 9b cells AG10 to AG60 will change colour if the total assets at year end for each asset class does not equal the corresponding values in column I in Schedule 9a. Schedule 9c cell P30 will change colour if P30 (overhead circuit length by terrain) does not equal P18 (overhead circuit length by operating voltage). Schedule 4 cells P99:P105 and P107 will change colour if the RAB values do not equal the corresponding values in table 4(ii).
Inserting Additional Rows and Columns
The templates for schedules 4, 5b, 5c, 5d, 5e, 5i, 6a, 8, 9d, and 9e may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar.
Additional rows in schedules 5c, 5i, 6a, and 9e must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Schedules 5d and 5e may require new cost or asset category rows to be inserted in allocation change tables 5d(iii) and 5e(ii). Accordingly, cell protection has been removed from rows 76 and 79 of the respective templates to allow blocks of rows to be copied. The four steps to add new cost category rows to table 5d(iii) are: Select Excel rows 67:74, copy, select Excel row 76, insert copied cells. Similarly, for table 5e(ii): Select Excel rows 70:77, copy, select Excel row 79, then insert copied cells.
The template for schedule 8 may require additional columns to be inserted between column P and U. To avoid interfering with the title block entries, these should be inserted to the left of column S. If inserting additional columns, the formulas for standard consumers total, non-standard consumers totals and total for all consumers will need to be copied into the cells of the added columns. The formulas can be found in the equivalent cells of the existing columns.
Disclosures by Sub-Network
If the supplier has sub-networks, schedules 8, 9a, 9b, 9c, 9e, and 10 must be completed for the network and for each sub-network. A copy of the schedule worksheet(s) must be made for each sub-network and named accordingly.
Schedule References
The references labelled 'sch ref' in the leftmost column of each template are consistent with the row references in the Electricity Distribution ID Determination 2012 (as issued on 1 October 2012). They provide a common reference between the rows in the determination and the template. Due to page formatting, the row reference sequences contained in the determination schedules are not necessarily contiguous.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.
Worksheet Completion Sequence
Calculation cells may show an incorrect value until precedent cell entries have been completed. Data entry may be assisted by completing the schedules in the following order:
1. Coversheet 2. Schedules 5a–5e 3. Schedules 6a and 6b 4. Schedule 8 5. Schedule 3 6. Schedule 4 7. Schedule 2 8. Schedule 7 9. Schedules 9a–9e 10. Schedule 10
Changes to disclosure year 2013
Clause 2.12 of the Electricity Distribution ID Determination 2012 does not apply for disclosure years 2014 and onwards. EDBs do not need to complete transitional schedules 5h and 5i. These schedules have been excluded from this version of the templates. All schedules in this workbook must now be completed in full and publicly disclosed.
Schedule 2: Report on Return on Investment
The ROI calculations are performed in this template.
All suppliers must complete tables 2(i) Return on Investment and 2(ii) Information Supporting the ROI.
Only suppliers who meet either of the two thresholds set out in subclause 2.3.3 of the Electricity Distribution Information Disclosure Determination 2012 need to complete table 2(iii) Information Supporting the Monthly ROI. We expect that most suppliers will generally not meet either threshold. You will need to work out if you met either threshold using your own tools (e.g. Excel) and do not need to disclosure these calculations. If you met either threshold you will need to provide a breakdown of five cash flow items on a month by month basis, as well as your opening revenue related working capital. The definitions for these items are the same as for the rest of the schedules. The values for assets commissioned and asset disposals should relate to the RAB (not the unallocated RAB).
The Excel worksheet uses several calculated cells beyond the rightmost edge of the template to calculate the monthly ROIs.
The prior year comparison information in the table 2(i) columns labelled CY-1 and CY-2 should be completed by copying the results from the previous year's disclosure.
Schedule 8: Report on Billed Quantities and Line Charge Revenues
This template should be completed in respect of each consumer groups or price category code (as applicable) that applied in the relevant disclosure year. The 'Average number of ICPs in disclosure year' column entries should be the arithmetic mean of monthly total ICPs (at month end).

## 1.Analytical Ratios
[6 empty] | Company Name | Alpine Energy Limitied
[6 empty] | For Year Ended | 2014-03-31
SCHEDULE 1: ANALYTICAL RATIOS
This schedule calculates expenditure, revenue and service ratios from the information disclosed. The disclosed ratios may vary for reasons that are company specific and, as a result, must be interpreted with care. The Commerce Commission will publish a summary and analysis of information disclosed in accordance with the ID determination. This will include information disclosed in accordance with this and other schedules, and information disclosed under the other requirements of the determination.
sch ref
7 | 1(i): Expenditure metrics
8 |  |  |  |  | Expenditure per GWh energy delivered to ICPs ($/GWh) | Expenditure per average no. of ICPs ($/ICP) | Expenditure per MW maximum coincident system demand ($/MW) | Expenditure per km circuit length ($/km) | Expenditure per MVA of capacity from EDB-owned distribution transformers ($/MVA)
9 |  | Operational expenditure |  |  | 21332.1584 | 486.1542 | 120144.7099 | 3684.333 | 36709.2023 | from S6b, S8, S9c, S9e
10 |  |  | Network |  | 8231.4365 | 187.5922 | 46360.2197 | 1421.673 | 14164.9739 | from S6b, S8, S9c, S9e
11 |  |  | Non-network |  | 13100.7219 | 298.5619 | 73784.4902 | 2262.66 | 22544.2284 | from S6b, S8, S9c, S9e
12
13 |  | Expenditure on assets |  | * | 26935.312 | 613.8485 | 151702.1946 | 4652.0684 | 46351.3254 | from S6a, S8, S9c, S9e
14 |  |  | Network | * | 25163.7273 | 573.4746 | 141724.464 | 4346.0934 | 43302.7141 | from S6a, S8, S9c, S9e
15 |  |  | Non-network |  | 1771.5847 | 40.3739 | 9977.7306 | 305.975 | 3048.6114 | from S6a, S8, S9c, S9e
16
17 | 1(ii): Revenue metrics
18 |  |  |  |  | Revenue per GWh energy delivered to ICPs ($/GWh) | Revenue per average no. of ICPs ($/ICP)
19 |  | Total consumer line charge revenue |  |  | 59174.0631 | 1348.561 |  |  |  | from S8
20 |  |  | Standard consumer line charge revenue |  | 72818.9986 | 1232.04 |  |  |  | from S8
21 |  |  | Non-standard consumer line charge revenue |  | 19867.931 | 916300.73 |  |  |  | from S8
22
23 | 1(iii): Service intensity measures
24
25 |  |  | Demand density |  | 30.6658 | Maximum coincident system demand per km circuit length (for supply) (kW/km) |  |  |  | from S9c & S9e
26 |  |  | Volume density |  | 172.7126 | Total energy delivered to ICPs per km circuit length (for supply) (MWh/km) |  |  |  | from S8 & S9c
27 |  |  | Connection point density |  | 7.5785 | Average number of ICPs per km circuit length (for supply) (ICPs/km) |  |  |  | from S8 & S9c
28 |  |  | Energy intensity |  | 22789.7311 | Total energy delivered to ICPs per Average number of ICPs (kWh/ICP) |  |  |  | from S8
29
30
31 | 1(iv): Composition of regulatory income
32 |  |  |  |  | ($000) | % of revenue
33 |  |  | Operational expenditure |  | 15271.5604 | 36.17% |  |  |  | from S3
34 |  |  | Pass-through and recoverable costs |  | 12953.0779 | 30.68% |  |  |  | from S3
35 |  |  | Total depreciation |  | 9784.5646 | 23.17% |  |  |  | from S3
36 |  |  | Total revaluation |  | 2346.8189 | 5.558% |  |  |  | from S3
37 |  |  | Regulatory tax allowance |  | 1139.0907 | 2.698% |  |  |  | from S3
38 |  |  | Regulatory profit/loss |  | 5419.0675 | 12.84% |  |  |  | from S3
39 |  | Total regulatory income |  |  | 42220.5423 |  |  |  |  | from S3
40
41 | 1(v): Reliability
42 |  |  |  |  | Interruptions per 100 circuit km
43 |  |  | Interruption rate |  | 10.0844 |  |  |  |  | from S9c & S10

## S2.Return on Investment
[7 empty] | Company Name | Alpine Energy Limitied
[7 empty] | For Year Ended | 2014-03-31
SCHEDULE 2: REPORT ON RETURN ON INVESTMENT
This schedule requires information on the Return on Investment (ROI) for the EDB relative to the Commerce Commission's estimates of post tax WACC and vanilla WACC. EDBs must calculate their ROI based on a monthly basis if required by clause 2.3.3 of the ID Determination or if they elect to. If an EDB makes this election, information supporting this calculation must be provided in 2(iii). EDBs must provide explanatory comment on their ROI in Schedule 14 (Mandatory Explanatory Notes). This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 2(i): Return on Investment | [6 empty] | CY-2 | CY-1 | Current Year CY
8 | [7 empty] | 2012-03-31 | 2013-03-31 | 2014-03-31
9 |  | Post tax WACC | [5 empty] | % | % | %
10 |  |  | ROI—comparable to a post tax WACC |  |  |  |  | 1.968% | 2.099% | 2.542% |  |  | from row 48 | J10 & K10 - from CY-1 ID disclosure
11
12 |  |  | Mid-point estimate of post tax WACC |  |  |  |  | 6.4% | 5.85% | 5.43% |  |  |  | J12 to L12 - from ComCom website (Cost of capital determination)
13 |  |  |  | 25th percentile estimate |  |  |  | 5.68% | 5.13% | 4.71% |  |  |  | J13 to L13 - from ComCom website (Cost of capital determination)
14 |  |  |  | 75th percentile estimate |  |  |  | 7.11% | 6.56% | 6.14% |  |  |  | J14 to L14 - from ComCom website (Cost of capital determination)
15
16
17 |  | Vanilla WACC
18 |  |  | ROI—comparable to a vanilla WACC |  |  |  |  | 2.795% | 2.876% | 3.227% |  |  | from row 42 | J18 & K18 - from CY-1 ID disclosure
19
20 |  |  | Mid-point estimate of vanilla WACC |  |  |  |  | 7.22% | 6.62% | 6.11% |  |  |  | J20 to L20 - from ComCom website (Cost of capital determination)
21 |  |  |  | 25th percentile estimate |  |  |  | 6.51% | 5.91% | 5.39% |  |  |  | J21 to L21 - from ComCom website (Cost of capital determination)
22 |  |  |  | 75th percentile estimate |  |  |  | 7.94% | 7.34% | 6.83% |  |  |  | J22 to L22 - from ComCom website (Cost of capital determination)
23
24 | 2(ii): Information Supporting the ROI | [7 empty] | ($000)
25
26 |  |  |  | Total opening RAB value |  |  |  | 153233.2191 |  |  |  |  | from S4 & to row 69
27 |  | plus |  | Opening deferred tax |  |  |  | -1026.7935 |  |  |  | Calculations for IRR *Do not delete* | from S5a
28 |  |  |  | Opening RIV |  |  |  |  | 152206.4256 |  | Negative Opening RIV | -152206.4256
29
30 |  |  |  | Operating surplus / (deficit) |  |  |  | 13995.904 |  |  |  |  | from S3
31 |  | less |  | Regulatory tax allowance |  |  |  | 1139.0907 |  |  |  |  | from S3
32 |  | less |  | Assets commissioned |  |  |  | 11151.5462 |  |  |  |  | from S4
33 |  | plus |  | Asset disposals |  |  |  | 168.4756 |  |  |  |  | from S4
34 |  |  | Notional net cash flows | [5 empty] | 1873.7427 |  | Notional net cash flows | 1873.7427
35
36 |  |  |  | Total closing RAB value |  |  |  | 156778.6951 |  |  |  |  | from S4
37 |  | less |  | Adjustment resulting from asset allocation |  |  |  | 0.15115 |  |  |  |  | from S4
38 |  | less |  | Lost and found assets adjustment |  |  |  | 0 |  |  |  |  | from S4
39 |  | plus |  | Closing deferred tax |  |  |  | -1563.7571 |  |  |  | Calculations for IRR *Do not delete* | from S5a
40 |  |  | Closing RIV | [5 empty] | 155214.7868 |  | Closing RIV | 155214.7868
41
42 |  | ROI—comparable to a vanilla WACC | [6 empty] | 3.227% |  | IRR | 1.601% | to row 18
43
44 |  |  |  | Leverage (%) |  |  |  |  | 44%
45 |  |  |  | Cost of debt assumption (%) |  |  |  |  | 5.56%
46 |  |  |  | Corporate tax rate (%) |  |  |  |  | 28%
47
48 |  | ROI—comparable to a post tax WACC | [6 empty] | 2.542% |  |  |  | to row 10
56 | 2(iii): Information Supporting the Monthly ROI
57
58 |  |  | Cash flows |  | ($000)
59 |  |  |  |  | Total regulatory income | Expenses | Tax payments | Assets commissioned | Asset disposals | Notional net cash flows | Notional net cash flows
60 |  |  |  | April | 3586.0871 | 2045.3315 | 102 | 288.577 | 0 | 1150.1785 | April | 1150.1785
61 |  |  |  | May | 3672.8541 | 2274.8843 | 94 | 318.0761 | 0 | 985.8936 | May | 985.8936
62 |  |  |  | June | 3157.6374 | 2506.285 | 37 | 1408.8085 | 27.5 | -766.956 | June | -766.956
63 |  |  |  | July | 3217.3133 | 2374.3276 | 46 | 1159.6029 | 27.5 | -335.1172 | July | -335.1172
64 |  |  |  | August | 3517.2147 | 2287.6748 | 86 | 69.2819 | 85.9756 | 1160.2336 | August | 1160.2336
65 |  |  |  | September | 3534.7778 | 3141.9487 | 15 | 24.7786 | 27.5 | 380.5505 | September | 380.5505
66 |  |  |  | October | 3505.4743 | 2483.2836 | 65 | 254.5168 | 0 | 702.6739 | October | 702.6739
67 |  |  |  | November | 3267.7614 | 2432.2503 | 44 | 865.9158 | 0 | -74.4047 | November | -74.4047
68 |  |  |  | December | 3426.4447 | 1693.9897 | 114 | 517.5198 | 0 | 1100.9352 | December | 1100.9352
69 |  |  |  | January | 3913.5732 | 2203.6633 | 119 | 418.1828 | 0 | 1172.7271 | January | 1172.7271
70 |  |  |  | February | 3636.3245 | 2276.7402 | 83 | 4351.1104 | 0 | -3074.526 | February | -3074.526
71 |  |  |  | March | 3785.0797 | 2504.2593 | 334 | 1475.1756 | 0 | -528.3552 | March | -528.3552
72 |  |  | Total |  | 42220.5423 | 28224.6384 | 1139 | 11151.5462 | 168.4756 | 1873.8334
73
74 |  |  |  |  | Opening / closing RAB | Adjustment resulting from asset allocation | Lost and found assets adjustment | Opening / closing deferred tax | Revenue related working capital | Total
75 |  |  |  | Monthly ROI - opening RIV | 153233.2191 |  |  | -1026.7935 | 3635.7778 | 155842.2034 | Negative Monthly ROI - opening RIV | -155842.2034 | from row 26 & S5a
76
77 |  |  |  | Monthly ROI -closing RIV | 156778.6951 | 0.15115 | 0 | -1563.7571 | 3785.0797 | 158999.8665
78 |  |  |  | Monthly ROI -closing RIV less term credit spread differential allowance | [5 empty] | 158999.8665 | Monthly ROI -closing RIV less term credit spread differential allowance + March |  | from S5c
79 |  |  | Monthly ROI—comparable to a vanilla WACC | [6 empty] | 3.279% |  | -155842.2034
80 | [11 empty] | 158471.5113
81 |  |  | Monthly ROI—comparable to a post-tax WACC | [6 empty] | 2.594%
82 | [10 empty] | IRR | 0.2693%
83 | 2(iv): Year-End ROI Rates for Comparison Purposes
84
85 |  |  | Year-end ROI—comparable to a vanilla WACC | [6 empty] | 3.435% |  |  | from S3
86
87 |  |  | Year-end ROI—comparable to a post-tax WACC | [6 empty] | 2.75%
88
89 |  | * these year-end ROI values are comparable to the ROI reported in pre 2012 disclosures by EDBs and do not represent the Commission's current view on ROI.

## S3.Regulatory Profit
[6 empty] | Company Name | Alpine Energy Limitied
[6 empty] | For Year Ended | 2014-03-31
SCHEDULE 3: REPORT ON REGULATORY PROFIT
This schedule requires information on the calculation of regulatory profit for the EDB for the disclosure year. All EDBs must complete 3(i), 3(iv) and 3(v) and must provide explanatory comment on their regulatory profit in Schedule 14 (Mandatory Explanatory Notes). Non-exempt EDBs must also complete sections 3(ii) and 3(iii). This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 3(i): Regulatory Profit | [7 empty] | ($000)
8 |  |  | Income
9 |  |  |  | Line charge revenue |  |  |  |  | 42362.3463 | from S8
10 |  | plus |  | Gains / (losses) on asset disposals |  |  |  |  | -168.4756
11 |  | plus |  | Other regulated income (other than gains / (losses) on asset disposals) |  |  |  |  | 26.6717
12
13 |  |  | Total regulatory income | [5 empty] | 42220.5423
14 |  |  | Expenses
15 |  | less |  | Operational expenditure |  |  |  |  | 15271.5604 | from S6b
17 |  | less |  | Pass-through and recoverable costs |  |  |  |  | 12953.0779 | from row 49
18
19 |  |  | Operating surplus / (deficit) | [5 empty] | 13995.904 | to S2
20
21 |  | less |  | Total depreciation |  |  |  |  | 9784.5646 | from S4
22
23 |  | plus |  | Total revaluation |  |  |  |  | 2346.8189 | from S4
24
25 |  |  | Regulatory profit / (loss) before tax & term credit spread differential allowance | [5 empty] | 6558.1583
26
27 |  | less |  | Term credit spread differential allowance |  |  |  |  | 0 | from S5c
28
29 |  |  | Regulatory profit / (loss) before tax | [5 empty] | 6558.1583 | to 5a
30
31 |  | less |  | Regulatory tax allowance |  |  |  |  | 1139.0907 | from S5a & to S2
32
33 |  |  | Regulatory profit / (loss) | [5 empty] | 5419.0675
34
35 | 3(ii): Pass-Through and Recoverable Costs | [7 empty] | ($000)
36 |  |  | Pass-through costs
37 |  |  |  | Rates |  |  |  | 58.5455
38 |  |  |  | Commerce Act levies |  |  |  | 86.8393
|  |  |  | Electricity Authority levies |  |  |  | 105.6495
40 |  |  |  | Other specified pass-through costs |  |  |  | 0
41 |  |  | Recoverable costs
42 |  |  |  | Net recoverable costs allowed under incremental rolling incentive scheme |  |  |  | 0
43 |  |  |  | Non-exempt EDB electricity lines service charge payable to Transpower |  |  |  | 12298.414
44 |  |  |  | Transpower new investment contract charges |  |  |  | 403.6298
45 |  |  |  | System operator services |  |  |  | 0
46 |  |  |  | Avoided transmission charge |  |  |  | 0
47 |  |  |  | Input Methodology claw-back |  |  |  | 0
48 |  |  |  | Recoverable customised price-quality path costs |  |  |  | 0
49 |  |  | Pass-through and recoverable costs | [5 empty] | 12953.0779 | to row 17
57 | 3(iii): Incremental Rolling Incentive Scheme | [6 empty] | ($000)
58 | [7 empty] | CY-1 | CY
59 | [7 empty] | 2013-03-31 | 2014-03-31
60 |  |  |  | Allowed controllable opex
61 |  |  |  | Actual controllable opex
62
63 |  |  |  | Incremental change in year
64
65 | [7 empty] | Previous years' incremental change | Previous years' incremental change adjusted for inflation
66 |  |  |  | CY-5 | 2009-03-31
67 |  |  |  | CY-4 | 2010-03-31
68 |  |  |  | CY-3 | 2011-03-31
69 |  |  |  | CY-2 | 2012-03-31
70 |  |  |  | CY-1 | 2013-03-31
71 |  |  | Net incremental rolling incentive scheme | [5 empty] | 0
72
73 |  |  | Net recoverable costs allowed under incremental rolling incentive scheme | [5 empty] | 0
74 | 3(iv): Merger and Acquisition Expenditure
75 |  |  |  | Merger and acquisition expenses
76
77 |  |  |  | Provide commentary on the benefits of merger and acquisition expenditure to the electricity distribution business, including required disclosures in accordance with section 2.7, in Schedule 14 (Mandatory Explanatory Notes)
78 | 3(v): Other Disclosures
79 |  |  |  | Self-insurance allowance |  |  |  | 0

## S4.RAB Value (Rolled Forward)
[11 empty] | Company Name | Alpine Energy Limitied
[11 empty] | For Year Ended | 2014-03-31
SCHEDULE 4: REPORT ON VALUE OF THE REGULATORY ASSET BASE (ROLLED FORWARD)
This schedule requires information on the calculation of the Regulatory Asset Base (RAB) value to the end of this disclosure year. This informs the ROI calculation in Schedule 2. EDBs must provide explanatory comment on the value of their RAB in Schedule 14 (Mandatory Explanatory Notes). This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 4(i): Regulatory Asset Base Value (Rolled Forward) | [8 empty] | RAB | RAB | RAB | RAB | RAB
8 | [8 empty] | for year ended | 2010-03-31 | 2011-03-31 | 2012-03-31 | 2013-03-31 | 2014-03-31
9 | [9 empty] | ($000) | ($000) | ($000) | ($000) | ($000)
10 |  |  | Total opening RAB value | [6 empty] | 127658.0267 | 126136.3721 | 130853.5736 | 131650.6646 | 153233.2191 | to S2 | L10 to O10 - from CY-1 ID disclosure
11
12 |  | less | Total depreciation | [6 empty] | 10171.6876 | 8318.1899 | 8948.8828 | 8058.7312 | 9784.5646 | from row 31 | L12 to O12 - from CY-1 ID disclosure
13
14 |  | plus | Total revaluations | [6 empty] | 2604.1221 | 3043.9824 | 2051.9509 | 1126.0098 | 2346.8189 | from row 33 | L14 to O14 - from CY-1 ID disclosure
15
16 |  | plus | Assets commissioned | [6 empty] | 6457.063 | 10258.097 | 7906.7193 | 29132.0366 | 11151.5462 | from row 38 & to S2 | L16 to O16 - from CY-1 ID disclosure
17
18 |  | less | Asset disposals | [6 empty] | 411.1521 | 266.688 | 212.6964 | 616.7607 | 168.4756 | from row 43& to S2 | L18 to O18 - from CY-1 ID disclosure
19
20 |  | plus | Lost and found assets adjustment | [6 empty] | 0 | 0 | 0 | 0 | 0 | from row 45& to S2 | L20 to O20 - from CY-1 ID disclosure
21
22 |  | plus | Adjustment resulting from asset allocation | [6 empty] | 0 | 0 | 0 | 0 | 0.15115 | from row 47 & to S2 | L22 to O22 - from CY-1 ID disclosure
23
24 |  |  | Total closing RAB value | [6 empty] | 126136.3721 | 130853.5736 | 131650.6646 | 153233.2191 | 156778.6951 | from row 49 to S2 | L24 to O24 - from CY-1 ID disclosure
25
26 | 4(ii): Unallocated Regulatory Asset Base
27 | [10 empty] | Unallocated RAB * |  | RAB
28 | [10 empty] | ($000) | ($000) | ($000) | ($000)
29 |  |  | Total opening RAB value | [8 empty] | 153233.2191 |  | 153233.2191 | to row 10 | N29 - from CY-1 ID disclosure
30 |  | less
31 |  |  | Total depreciation | [8 empty] | 9784.5646 |  | 9784.5646 | from row 83
32 |  | plus
33 |  |  | Total revaluations | [8 empty] | 2346.8189 |  | 2346.8189 | from row 64
34 |  | plus
35 |  |  |  | Assets commissioned (other than below) | [6 empty] | 834.1195 |  | 834.1195
36 |  |  |  | Assets acquired from a regulated supplier | [6 empty] | 0 |  | 0
37 |  |  |  | Assets acquired from a related party | [6 empty] | 10317.4267 |  | 10317.4267
38 |  |  | Assets commissioned | [8 empty] | 11151.5462 |  | 11151.5462 | to row 16
39 |  | less
40 |  |  |  | Asset disposals (other than below) | [6 empty] | 168.4756 |  | 168.4756
41 |  |  |  | Asset disposals to a regulated supplier | [6 empty] | 0 |  | 0
42 |  |  |  | Asset disposals to a related party | [6 empty] | 0 |  | 0
43 |  |  | Asset disposals | [8 empty] | 168.4756 |  | 168.4756 | to row 18
44
45 |  | plus | Lost and found assets adjustment | [8 empty] | 0 |  | 0 | to row 20
46
47 |  | plus | Adjustment resulting from asset allocation | [10 empty] | 0.15115 | to row 22
48
49 |  |  | Total closing RAB value | [8 empty] | 156778.5439 |  | 156778.6951 | from S5e
50 | * The 'unallocated RAB' is the total value of those assets used wholly or partially to provide electricity distribution services without any allowance being made for the allocation of costs to non-regulated services. The RAB value represents the value of these assets after applying this cost allocation. Neither value includes works under construction.
58 | 4(iii): Calculation of Revaluation Rate and Revaluation of Assets
59
60 |  |  |  | CPI4 | [9 empty] | 1192 |  | from SE9A Index column - CPI table (Statistics NZ Website)
61 |  |  |  | CPI4-4 | [9 empty] | 1174 |  | from SE9A Index column - CPI table (Statistics NZ Website)
62 |  |  |  | Revaluation rate (%) | [9 empty] | 1.533%
63
64 | [10 empty] | Unallocated RAB * |  | RAB
65 | [10 empty] | ($000) | ($000) | ($000) | ($000)
66 |  |  |  | Total opening RAB value | [6 empty] | 153233.2191 |  | 153233.2191 |  | to row 10
67 |  | less |  | Opening RAB value of fully depreciated, disposed and lost assets | [6 empty] | 168.4756 |  | 168.4756
68
69 |  |  |  | Total opening RAB value subject to revaluation | [6 empty] | 153064.7434 |  | 153064.7434
70 |  |  | Total revaluations | [8 empty] | 2346.8189 |  | 2346.8189 | to row 33 & S3
71
72 | 4(iv): Roll Forward of Works Under Construction
73 | [10 empty] | Unallocated works under construction |  | Allocated works under construction
74 |  |  | Works under construction—preceding disclosure year | [8 empty] | 4045.1471 |  | 4045.1471 |  | from CY-1 ID disclosure
75 |  | plus |  | Capital expenditure | [6 empty] | 14228.6486 |  | 14228.6486 |  | from S6a
76 |  | less |  | Assets commissioned | [6 empty] | 11151.5462 |  | 11151.5462 |  | from row 38
77 |  | plus |  | Adjustment resulting from asset allocation | [8 empty] | 0
78 |  |  | Works under construction - current disclosure year | [8 empty] | 7122.2495 |  | 7122.2495
79
80 |  |  |  | Highest rate of capitalised finance applied | [9 empty] | 0%
88 | 4(v): Regulatory Depreciation
89 | [10 empty] | Unallocated RAB * |  | RAB
90 | [10 empty] | ($000) | ($000) | ($000) | ($000)
91 |  |  |  | Depreciation - standard | [6 empty] | 9430.785 |  | 9430.785
92 |  |  |  | Depreciation - no standard life assets | [6 empty] | 353.7796 |  | 353.7796
93 |  |  |  | Depreciation - modified life assets | [6 empty] | 0 |  | 0
94 |  |  |  | Depreciation - alternative depreciation in accordance with CPP | [6 empty] | 0 |  | 0
95 |  |  | Total depreciation | [8 empty] | 9784.5646 |  | 9784.5646 | to row 31 & S3
96
97 | 4(vi): Disclosure of Changes to Depreciation Profiles | [8 empty] | ($000 unless otherwise specified)
98 |  |  |  | Asset or assets with changes to depreciation* |  |  |  |  | Reason for non-standard depreciation (text entry) |  |  | Depreciation charge for the period (RAB) | Closing RAB value under 'non-standard' depreciation | Closing RAB value under 'standard' depreciation
99
100
101
102
103
104
105
106
* include additional rows if needed
107 | 4(vii): Disclosure by Asset Category
108 |  |  |  |  | ($000 unless otherwise specified) | [10 empty] | Column conditional formatting
109 |  |  |  |  | Subtransmission lines | Subtransmission cables | Zone substations | Distribution and LV lines | Distribution and LV cables | Distribution substations and transformers | Distribution switchgear | Other network assets | Non-network assets | Total |  | Table 4(ii) | Agrees with Table 4(ii)
110 |  |  | Total opening RAB value |  | 8400.754 | 609.2644 | 25856.6115 | 41018.4888 | 45572.8767 | 22709.7311 | 3951.3124 | 4354.4177 | 759 | 153232.4567 |  | 153233.2191 | FALSE
111 |  | less |  | Total depreciation | 380.5595 | 23.0134 | 1552.3744 | 3639.6983 | 1682.0113 | 1630.5578 | 290.3986 | 232.1717 | 353.7796 | 9784.5646 |  | 9784.5646 | TRUE
112 |  | plus |  | Total revaluations | 128.802 | 9.3414 | 395.5421 | 628.9036 | 698.7324 | 348.1901 | 60.5823 | 65.0763 | 12 | 2347.1701 |  | 2346.8189 | TRUE
113 |  | plus |  | Assets commissioned | 3544.7651 | 3.5345 | 2654.1255 | 1947.0072 | 490.3927 | 361.316 | 650.4421 | 231.6965 | 1268.2665 | 11151.5462 |  | 11151.5462 | TRUE
114 |  | less |  | Asset disposals | 0 | 0 | 58.4756 | 0 | 0 | 0 | 0 | 110 | 0 | 168.4756 |  | 168.4756 | TRUE
115 |  | plus |  | Lost and found assets adjustment | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | TRUE
116 |  | plus |  | Adjustment resulting from asset allocation | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.15115 | TRUE
117 |  | plus |  | Asset category transfers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
118 |  |  | Total closing RAB value |  | 11693.7616 | 599.1269 | 27295.4291 | 39954.7014 | 45079.9904 | 21788.6794 | 4371.9383 | 4309.0187 | 1685.487 | 156778.1328 |  | 156778.6951 | FALSE
119
120 |  |  | Asset Life
121 |  |  |  | Weighted average remaining asset life | 35.5883 | 31.0037 | 34.4829 | 29.5246 | 41.0045 | 27.1132 | 33.3933 | 23.4055 | 24.9844 | (years)
122 |  |  |  | Weighted average expected total asset life | 51 | 45 | 40.2999 | 53.2147 | 55.2597 | 45 | 44.1438 | 35.0928 | 32.7623 | (years)

## S5a.Regulatory Tax Allowance
[5 empty] | Company Name | Alpine Energy Limitied
[5 empty] | For Year Ended | 2014-03-31
SCHEDULE 5a: REPORT ON REGULATORY TAX ALLOWANCE
This schedule requires information on the calculation of the regulatory tax allowance. This information is used to calculate regulatory profit/loss in Schedule 3 (regulatory profit). EDBs must provide explanatory commentary on the information disclosed in this schedule, in Schedule 14 (Mandatory Explanatory Notes). This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 5a(i): Regulatory Tax Allowance | [6 empty] | ($000)
8 |  |  | Regulatory profit / (loss) before tax |  |  |  |  | 6558.1583 | from S3
9
10 |  | plus |  | Income not included in regulatory profit / (loss) before tax but taxable |  |  | 0 | *
11 |  |  |  | Expenditure or loss in regulatory profit / (loss) before tax but not deductible |  |  | 6.436 | *
12 |  |  |  | Amortisation of initial differences in asset values |  |  | 2834.604 |  | from row 37
13 |  |  |  | Amortisation of revaluations |  |  | 739.7311 |  | from row 49
14 | [7 empty] | 3580.771
15
16 |  | less |  | Income included in regulatory profit / (loss) before tax but not taxable |  |  | 2347.1701 | * |  | Total revaluation from S3 (T23) must be included in I16
17 |  |  |  | Discretionary discounts and consumer rebates |  |  | 0
18 |  |  |  | Expenditure or loss deductible but not in regulatory profit / (loss) before tax** |  |  | 0 | *
19 |  |  |  | Notional deductible interest |  |  | 3723.578
20 | [7 empty] | 6070.7481
21
22 |  |  | Regulatory taxable income |  |  |  |  | 4068.1812
23
24 |  | less |  | Utilised tax losses |  |  | 0
25 |  |  |  | Regulatory net taxable income |  |  |  | 4068.1812
26
27 |  |  |  | Corporate tax rate (%) |  |  | 28%
28 |  |  | Regulatory tax allowance |  |  |  |  | 1139.0907 | to S3
29
30 | * Workings to be provided in Schedule 14
31 | ** Excluding discretionary discounts and consumer rebates
32 | 5a(ii): Disclosure of Permanent Differences
33 |  |  |  | In Schedule 14, Box 5, provide descriptions and workings of items recorded in the asterisked categories in Schedule 5a(i).
34 | 5a(iii): Amortisation of Initial Difference in Asset Values | [6 empty] | ($000)
35
36 |  |  |  | Opening unamortised initial differences in asset values |  |  | 58311.8695 |  |  | from CY-1 ID disclosure
37 |  |  |  | Amortisation of initial differences in asset values |  |  | 2834.604 |  | to row 12
38 |  |  |  | Adjustment for unamortised initial differences in assets acquired |  |  | 0
39 |  |  |  | Adjustment for unamortised initial differences in assets disposed |  |  | 139.1974
40 |  |  |  | Closing unamortised initial differences in asset values |  |  |  | 55338.0681
41
42 |  |  |  | Opening weighted average remaining asset life (years) |  |  |  | 20.5714
43 | 5a(iv): Amortisation of Revaluations | [6 empty] | ($000)
44
45 |  |  |  | Opening Sum of RAB values without revaluations |  |  | 145352.6386
46
47 |  |  |  | Adjusted depreciation |  |  | 9044.8335
48 |  |  |  | Total depreciation |  |  | 9784.5646 |  | from S4
49 |  |  |  | Amortisation of revaluations |  |  |  | 739.7311 | to row 13
57 | 5a(v): Reconciliation of Tax Losses | [6 empty] | ($000)
58
59 |  |  | Opening tax losses |  |  |  | 0 |  |  | from CY-1 ID disclosure
60 |  | plus |  | Current period tax losses |  |  | 0
61 |  | less |  | Utilised tax losses |  |  | 0
62 |  |  | Closing tax losses |  |  |  |  | 0
63 | 5a(vi): Calculation of Deferred Tax Balance | [6 empty] | ($000)
64
65 |  |  | Opening deferred tax |  |  |  | -1026.7935 |  | to S2
66
67 |  | plus |  | Tax effect of adjusted depreciation |  |  | 2532.5534
68
69 |  | less |  | Tax effect of total tax depreciation |  |  | 2326.2394
70
71 |  | plus |  | Tax effect of other temporary differences* |  |  | 50.4115
72
73 |  | less |  | Tax effect of amortisation of initial differences in asset values |  |  | 793.6891
74
75 |  | plus |  | Deferred tax balance relating to assets acquired in the disclosure year |  |  | 0
76
77 |  | less |  | Deferred tax balance relating to assets disposed in the disclosure year |  |  | 0
78
79 |  | plus |  | Deferred tax cost allocation adjustment |  |  | 0
80
81 |  |  | Closing deferred tax |  |  |  |  | -1563.7571 | to S2
82
83 | 5a(vii): Disclosure of Temporary Differences
84 |  |  |  | In Schedule 14, Box 6, provide descriptions and workings of items recorded in the asterisked category in Schedule 5a(vi) (Tax effect of other temporary differences).
85
86 | 5a(viii): Regulatory Tax Asset Base Roll-Forward
87 | [7 empty] | ($000)
88 |  |  | Opening sum of regulatory tax asset values |  |  |  | 86577.3647 |  |  | from CY-1 ID disclosure
89 |  | less |  | Tax depreciation |  |  | 8307.9978
90 |  | plus |  | Regulatory tax asset value of assets commissioned |  |  | 11105.7209
91 |  | less |  | Regulatory tax asset value of asset disposals |  |  | 619.7274
92 |  | plus |  | Lost and found assets adjustment |  |  | 0
93 |  | plus |  | Other adjustments to the RAB tax value |  |  | 443.7996
94 |  |  | Closing sum of regulatory tax asset values |  |  |  |  | 89199.16

## S5b.Related Party Transactions
|  |  |  | Company Name | Alpine Energy Limitied
|  |  |  | For Year Ended | 2014-03-31
SCHEDULE 5b: REPORT ON RELATED PARTY TRANSACTIONS
This schedule provides information on the valuation of related party transactions, in accordance with section 2.3.6 and 2.3.7 of the ID determination. This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 5b(i): Summary—Related Party Transactions |  |  |  | ($000)
8 |  | Total regulatory income |  |  | 0
9 |  | Operational expenditure |  |  | 6511.4986
10 |  | Capital expenditure |  |  | 12040.4267
11 |  | Market value of asset disposals |  |  | 0
12 |  | Other related party transactions |  |  | 0
13 | 5b(ii): Entities Involved in Related Party Transactions
14 |  | Name of related party |  | Related party relationship
15 |  | Netcon Ltd |  | Wholly owned subsidiary and contractor
16
17
18
19
20 |  | * include additional rows if needed
21 | 5b(iii): Related Party Transactions
22 |  | Name of related party | Related party transaction type | Description of transaction |  | Value of transaction ($000) | Basis for determining value
23 |  | Netcon Ltd | Opex | Maintenance of Assets |  | 6511.4986 | Netcon Charge Labour and Plant at market Values with materials having a markup of 15%
24 |  | Netcon Ltd | Capex | Subtransmission assets |  | 289.1865
25 |  | Netcon Ltd | Capex | Zone Substations |  | 6402.7464
26 |  | Netcon Ltd | Capex | Distribution and LV Lines |  | 1333.7952
27 |  | Netcon Ltd | Capex | Distribution and LV Cables |  | 3345.4198
28 |  | Netcon Ltd | Capex | Distribution Substations and Transformers |  | 77.3551
29 |  | Netcon Ltd | Capex | Distribution Switchgear |  | 294.3606
30 |  | Netcon Ltd | Capex | Other System Fixed Assets (as per the ODV Handbook) |  | 0
31 |  | Netcon Ltd | Capex | Assets capitalised to the FAR but not initial processed to WIP |  | 297.563
32 |  |  | [Select one]
33 |  |  | [Select one]
34 |  |  | [Select one]
35 |  |  | [Select one]
36 |  |  | [Select one]
37 |  |  | [Select one]
* include additional rows if needed

## S5c.TCSD Allowance
[9 empty] | Company Name | Alpine Energy Limitied
[9 empty] | For Year Ended | 2014-03-31
SCHEDULE 5c: REPORT ON TERM CREDIT SPREAD DIFFERENTIAL ALLOWANCE
This schedule is only to be completed if, as at the date of the most recently published financial statements, the weighted average original tenor of the debt portfolio (both qualifying debt and non-qualifying debt) is greater than five years. This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7
8 | 5c(i): Qualifying Debt (may be Commission only)
9
10 |  |  | Issuing party | Issue date | Pricing date | Original tenor (in years) | Coupon rate (%) | Book value at issue date (NZD) | Book value at date of financial statements (NZD) | Term Credit Spread Difference | Cost of executing an interest rate swap | Debt issue cost readjustment
11
12
13
14
15
16 |  |  | * include additional rows if needed | [5 empty] | 0 | 0 | 0 | 0 | to row 20
17
18 | 5c(ii): Attribution of Term Credit Spread Differential
19
20 |  | Gross term credit spread differential |  |  |  | 0 | [6 empty] | from row 16
21
22 |  |  | Total book value of interest bearing debt
23 |  |  | Leverage |  | 44%
24 |  |  | Average opening and closing RAB values
25 |  | Attribution Rate (%) |  |  |  | 0%
26
27 |  | Term credit spread differential allowance |  |  |  | 0 | [6 empty] | to S3

## S5d.Cost Allocations
[6 empty] | Company Name | Alpine Energy Limitied
[6 empty] | For Year Ended | 2014-03-31
SCHEDULE 5d: REPORT ON COST ALLOCATIONS
This schedule provides information on the allocation of operational costs. EDBs must provide explanatory comment on their cost allocation in Schedule 14 (Mandatory Explanatory Notes), including on the impact of any reclassifications. This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 5d(i): Operating Cost Allocations
8 |  |  |  |  | Value allocated ($000s)
9 |  |  |  |  | Arm's length deduction | Electricity distribution services | Non-electricity distribution services | Total | OVABAA allocation increase ($000s)
10 |  | Service interruptions and emergencies
11 |  |  |  | Directly attributable |  | 1978.7777
12 |  |  |  | Not directly attributable |  |  |  | 0
13 |  |  | Total attributable to regulated service |  |  | 1978.7777
14 |  | Vegetation management
15 |  |  |  | Directly attributable |  | 110.4575
16 |  |  |  | Not directly attributable |  |  |  | 0
17 |  |  | Total attributable to regulated service |  |  | 110.4575
18 |  | Routine and corrective maintenance and inspection
19 |  |  |  | Directly attributable |  | 3231.8705
20 |  |  |  | Not directly attributable |  |  |  | 0
21 |  |  | Total attributable to regulated service |  |  | 3231.8705
22 |  | Asset replacement and renewal
23 |  |  |  | Directly attributable |  | 571.7288
24 |  |  |  | Not directly attributable |  |  |  | 0
25 |  |  | Total attributable to regulated service |  |  | 571.7288
26 |  | System operations and network support
27 |  |  |  | Directly attributable |  | 4977.9269
28 |  |  |  | Not directly attributable |  |  |  | 0
29 |  |  | Total attributable to regulated service |  |  | 4977.9269
30 |  | Business support
31 |  |  |  | Directly attributable |  | 4400.799
32 |  |  |  | Not directly attributable |  |  |  | 0
33 |  |  | Total attributable to regulated service |  |  | 4400.799
34
35 |  | Operating costs directly attributable |  |  |  | 15271.5604
36 |  | Operating costs not directly attributable |  |  | 0 | 0 | 0 | 0 | 0
37 |  | Operating expenditure |  |  |  | 15271.5604
45 | 5d(ii): Other Cost Allocations
46 |  | Pass through and recoverable costs
47 |  | Pass through costs
48 |  |  |  | Directly attributable |  | 251.0342
49 |  |  |  | Not directly attributable |  | 0
50 |  |  | Total attributable to regulated service |  |  | 251.0342
51 |  | Recoverable costs
52 |  |  |  | Directly attributable |  | 12702.0437
53 |  |  |  | Not directly attributable |  | 0
54 |  |  | Total attributable to regulated service |  |  | 12702.0437
55
56 | 5d(iii): Changes in Cost Allocations* † | [5 empty] | ($000)
57 | [6 empty] | CY-1 | Current Year (CY)
58 |  |  | Change in cost allocation 1 |  |  |  | 2013-03-31 | 2014-03-31
59 |  |  |  | Cost category |  | Original allocation
60 |  |  |  | Original allocator or line items |  | New allocation
61 |  |  |  | New allocator or line items |  | Difference | 0 | 0
62
63 |  |  |  | Rationale for change
64
65 | [6 empty] | CY-1 | Current Year (CY)
66 |  |  | Change in cost allocation 2 |  |  |  | 2013-03-31 | 2014-03-31
67 |  |  |  | Cost category |  | Original allocation
68 |  |  |  | Original allocator or line items |  | New allocation
69 |  |  |  | New allocator or line items |  | Difference | 0 | 0
70
71 |  |  |  | Rationale for change
72
73 | [6 empty] | CY-1 | Current Year (CY)
74 |  |  | Change in cost allocation 3 |  |  |  | 2013-03-31 | 2014-03-31
75 |  |  |  | Cost category |  | Original allocation
76 |  |  |  | Original allocator or line items |  | New allocation
77 |  |  |  | New allocator or line items |  | Difference | 0 | 0
78
79 |  |  |  | Rationale for change
80
81
82 | * a change in cost allocation must be completed for each cost allocator change that has occurred in the disclosure year. A movement in an allocator metric is not a change in allocator or component.
† include additional rows if needed

## S5e.Asset Allocations
[5 empty] | Company Name | Alpine Energy Limitied
[5 empty] | For Year Ended | 2014-03-31
SCHEDULE 5e: REPORT ON ASSET ALLOCATIONS
This schedule requires information on the allocation of asset values. This information supports the calculation of the RAB value in Schedule 4. EDBs must provide explanatory comment on their cost allocation in Schedule 14 (Mandatory Explanatory Notes), including on the impact of any changes in asset allocations. This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 5e(i):Regulated Service Asset Values
8 |  |  |  |  | Value allocated ($000s)
9 |  |  |  |  | Electricity distribution services
10 |  | Subtransmission lines
11 |  |  |  | Directly attributable | 11693.9596
12 |  |  |  | Not directly attributable
13 |  |  | Total attributable to regulated service |  | 11693.9596
14 |  | Subtransmission cables
15 |  |  |  | Directly attributable | 598.7856
16 |  |  |  | Not directly attributable
17 |  |  | Total attributable to regulated service |  | 598.7856
18 |  | Zone substations
19 |  |  |  | Directly attributable | 27295.887
20 |  |  |  | Not directly attributable
21 |  |  | Total attributable to regulated service |  | 27295.887
22 |  | Distribution and LV lines
23 |  |  |  | Directly attributable | 39954.7978
24 |  |  |  | Not directly attributable
25 |  |  | Total attributable to regulated service |  | 39954.7978
26 |  | Distribution and LV cables
27 |  |  |  | Directly attributable | 45079.9904
28 |  |  |  | Not directly attributable
29 |  |  | Total attributable to regulated service |  | 45079.9904
30 |  | Distribution substations and transformers
31 |  |  |  | Directly attributable | 21788.4893
32 |  |  |  | Not directly attributable
33 |  |  | Total attributable to regulated service |  | 21788.4893
34 |  | Distribution switchgear
35 |  |  |  | Directly attributable | 4372.356
36 |  |  |  | Not directly attributable
37 |  |  | Total attributable to regulated service |  | 4372.356
38 |  | Other network assets
39 |  |  |  | Directly attributable | 4308.9425
40 |  |  |  | Not directly attributable
41 |  |  | Total attributable to regulated service |  | 4308.9425
42 |  | Non-network assets
43 |  |  |  | Directly attributable | 1685.487
44 |  |  |  | Not directly attributable
45 |  |  | Total attributable to regulated service |  | 1685.487
46
47 |  | Regulated service asset value directly attributable |  |  | 156778.6951
48 |  | Regulated service asset value not directly attributable |  |  | 0
49 |  | Total closing RAB value |  |  | 156778.6951 |  |  | to S4
57 | 5e(ii): Changes in Asset Allocations* † |  |  |  |  | ($000)
58 | [5 empty] | CY-1 | Current Year (CY)
59 | [5 empty] | 2013-03-31 | 2014-03-31
60 |  |  | Change in asset value allocation 1
61 |  |  |  | Asset category | Original allocation
62 |  |  |  | Original allocator or line items | New allocation
63 |  |  |  | New allocator or line items | Difference | 0 | 0
64
65 |  |  |  | Rationale for change
66
67 | [5 empty] | CY-1 | Current Year (CY)
68 |  |  | Change in asset value allocation 2 |  |  | 2013-03-31 | 2014-03-31
69 |  |  |  | Asset category | Original allocation
70 |  |  |  | Original allocator or line items | New allocation
71 |  |  |  | New allocator or line items | Difference | 0 | 0
72
73 |  |  |  | Rationale for change
74
75
76 | [5 empty] | CY-1 | Current Year (CY)
77 |  |  | Change in asset value allocation 3 |  |  | 2013-03-31 | 2014-03-31
78 |  |  |  | Asset category | Original allocation
79 |  |  |  | Original allocator or line items | New allocation
80 |  |  |  | New allocator or line items | Difference | 0 | 0
81
82 |  |  |  | Rationale for change
83
84
85 | * a change in asset allocation must be completed for each allocator or component change that has occurred in the disclosure year. A movement in an allocator metric is not a change in allocator or component.
† include additional rows if needed

## S6a.Actual Expenditure Capex
[6 empty] | Company Name | Alpine Energy Limitied
[6 empty] | For Year Ended | 2014-03-31
SCHEDULE 6a: REPORT ON CAPITAL EXPENDITURE FOR THE DISCLOSURE YEAR
This schedule requires a breakdown of capital expenditure on assets incurred in the disclosure year, including any assets in respect of which capital contributions are received, but excluding assets that are vested assets. Information on expenditure on assets must be provided on an accounting accruals basis and must exclude finance costs. EDBs must provide explanatory comment on their expenditure on assets in Schedule 14 (Explanatory Notes to Templates). This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 6a(i): Expenditure on Assets | [6 empty] | ($000) | ($000)
8 |  |  |  | Consumer connection |  |  |  | * | 3700.7889 | from row 38 & to S7
9 |  |  |  | System growth |  |  |  | * | 8775.3786 | from row 52 & to S7
10 |  |  |  | Asset replacement and renewal |  |  |  |  | 2688.1421 | from row 52 & to S7
11 |  |  |  | Asset relocations |  |  |  |  | 264.9422 | from row 65 & to S7
12 |  |  |  | Reliability, safety and environment:
13 |  |  |  |  | Quality of supply |  |  | 86.4254 |  | from row 78 & to S7
14 |  |  |  |  | Legislative and regulatory |  |  | 0 |  | from row 90 & to S7
15 |  |  |  |  | Other reliability, safety and environment |  |  | 2498.8799 |  | from row 102 & to S7
16 |  |  |  | Total reliability, safety and environment |  |  |  |  | 2585.3053
17 |  |  | Expenditure on network assets | [5 empty] | 18014.5569
18 |  |  |  | Non-network assets |  |  |  |  | 1268.2665 | from row 128 & to S7
19
20 |  |  | Expenditure on assets | [5 empty] | 19282.8235
21 |  | plus |  | Cost of financing |  |  |  |  | 0
22 |  | less |  | Value of capital contributions |  |  |  |  | 5054.1749
23 |  | plus |  | Value of vested assets |  |  |  |  | 0
24
25 |  |  | Capital expenditure | [5 empty] | 14228.6486 | to S4
26 | 6a(ii): Subcomponents of Expenditure on Assets (where known) | [7 empty] | ($000)
27 |  |  |  |  | Energy efficiency and demand side management, reduction of energy losses |  |  |  | 11.6526 | to S7
28 |  |  |  |  | Overhead to underground conversion |  |  |  | 236.1932 | to S7
29 |  |  |  |  | Research and development |  |  |  | 74 | to S7
30 | 6a(iii): Consumer Connection
31 |  |  |  |  | Consumer types defined by EDB* |  |  | ($000) | ($000)
32 |  |  |  |  | 6a(iii): Consumer Connection
33 |  |  |  |  | [EDB consumer type]
34 |  |  |  |  | [EDB consumer type]
35 |  |  |  |  | [EDB consumer type]
36 |  |  |  |  | [EDB consumer type]
37 |  |  |  |  | * include additional rows if needed
38 |  |  |  | Consumer connection expenditure |  |  |  |  | 3700.7889 | to row 8
39
40 |  | less |  |  | Capital contributions funding consumer connection expenditure |  |  | 1038.4308
41 |  |  |  | Consumer connection less capital contributions |  |  |  |  | 2662.358
42 | 6a(iv): System Growth and Asset Replacement and Renewal | [6 empty] | System Growth | Asset Replacement and Renewal
43
44 | [7 empty] | ($000) | ($000)
45 |  |  |  |  | Subtransmission |  |  | 4033.5014 | 355.0585
46 |  |  |  |  | Zone substations |  |  | 151.6722 | 424.0922
47 |  |  |  |  | Distribution and LV lines |  |  | 414.8648 | 867.4311
48 |  |  |  |  | Distribution and LV cables |  |  | 83.1814 | 127.2968
49 |  |  |  |  | Distribution substations and transformers |  |  | 3618.3224 | 251.0678
50 |  |  |  |  | Distribution switchgear |  |  | 706.0266 | 315.9694
51 |  |  |  |  | Other network assets |  |  | -232.1901 | 347.2263
52 |  |  |  | System growth and asset replacement and renewal expenditure |  |  |  | 8775.3786 | 2688.1421 | to row 9
53 |  | less |  |  | Capital contributions funding system growth and asset replacement and renewal |  |  | 2462.3463 | 754.285
54 |  |  |  | System growth and asset replacement and renewal less capital contributions |  |  |  | 6313.0323 | 1933.857
55
56 | 6a(v): Asset Relocations
57 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
58 |  |  |  |  | Line recloser new locations |  |  | 25.7758
59 |  |  |  |  | Network - New Subdivisions & extensions for new services |  |  | 43.5761
60 |  |  |  |  | Network - Various O/H new builds & upgrades |  |  | 195.5902
61 |  |  |  |  | [Description of material project or programme] |  |  | N/A
62 |  |  |  |  | [Description of material project or programme] |  |  | N/A
63 |  |  |  |  | * include additional rows if needed
64 |  |  |  |  | All other asset relocations projects or programmes |  |  | 0
65 |  |  |  | Asset relocations expenditure |  |  |  |  | 264.9422 | to row 11
66 |  | less |  |  | Capital contributions funding asset relocations |  |  | 74.342
67 |  |  |  | Asset relocations less capital contributions |  |  |  |  | 190.6001
75 | 6a(vi): Quality of Supply
76 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
77 |  |  |  |  | Non Budgeted Items |  |  | 0.183
78 |  |  |  |  | Network - Distribution Sub refurbishment |  |  | 2.6482
[5 empty] | Network - Reclosers New |  |  | 8.6264
[5 empty] | Network - Zone Substation Protection replacement |  |  | 14.0418
79 |  |  |  |  | Network - New Equipment |  |  | 25.1965
80 |  |  |  |  | Equipment |  |  | 34.447
81 |  |  |  |  | Network - Underground Cable Upgrades (G) |  |  | 1.2825
82 |  |  |  |  | * include additional rows if needed
83 |  |  |  |  | All other quality of supply projects or programmes |  |  | 0
84 |  |  |  | Quality of supply expenditure |  |  |  |  | 86.4254 | to row 13
85 |  | less |  |  | Capital contributions funding quality of supply |  |  | 24.2507
86 |  |  |  | Quality of supply less capital contributions |  |  |  |  | 62.1746
87 | 6a(vii): Legislative and Regulatory
88 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
89 |  |  |  |  | [Description of material project or programme]
90 |  |  |  |  | [Description of material project or programme]
91 |  |  |  |  | [Description of material project or programme]
92 |  |  |  |  | [Description of material project or programme]
93 |  |  |  |  | [Description of material project or programme]
94 |  |  |  |  | * include additional rows if needed
95 |  |  |  |  | All other legislative and regulatory projects or programmes
96 |  |  |  | Legislative and regulatory expenditure |  |  |  |  | 0 | to row 14
97 |  | less |  |  | Capital contributions funding legislative and regulatory
98 |  |  |  | Legislative and regulatory less capital contributions |  |  |  |  | 0
99 | 6a(viii): Other Reliability, Safety and Environment
100 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
101 |  |  |  |  | Overhead Lines, new, refurbished and upgraded |  |  | 46.3098
[5 empty] | Customer connections, incuding new subdivisions and externsions for new services |  |  | 38.4601
[5 empty] | Metering and relays |  |  | 0
102 |  |  |  |  | Distribution Substations, including transformer, regulators, ring main units, etc. |  |  | 207.1856
103 |  |  |  |  | Underground cables, including overhead to underground conversions |  |  | 39.6065
104 |  |  |  |  | Zone substations, including load control plants |  |  | 129.0628
105 |  |  |  |  | System development |  |  | 395.8546
106 |  |  |  |  | * include additional rows if needed
107 |  |  |  |  | All other reliability, safety and environment projects or programmes |  |  | 1642.4005
108 |  |  |  | Other reliability, safety and environment expenditure |  |  |  |  | 2498.8799 | to row 15
109 |  | less |  |  | Capital contributions funding other reliability, safety and environment |  |  | 700.5199
110 |  |  |  | Other reliability, safety and environment less capital contributions |  |  |  |  | 1798.36
111
112 | 6a(ix): Non-Network Assets
113 |  |  | Routine expenditure
114 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
115 |  |  |  |  | LandB |  |  | 421.4193
116 |  |  |  |  | Plant |  |  | 631.6302
117 |  |  |  |  | Software |  |  | 39.7608
118 |  |  |  |  | Vehicle |  |  | 175.4563
119 |  |  |  |  | [Description of material project or programme]
120 |  |  |  |  | * include additional rows if needed
121 |  |  |  |  | All other routine expenditure projects or programmes |  |  | 0
122 |  |  |  | Routine expenditure |  |  |  |  | 1268.2665
123 |  |  | Atypical expenditure
124 |  |  |  |  | Project or programme* |  |  | ($000) | ($000)
125
126 |  |  |  |  | [Description of material project or programme]
127 |  |  |  |  | [Description of material project or programme]
128 |  |  |  |  | [Description of material project or programme]
129 |  |  |  |  | [Description of material project or programme]
130 |  |  |  |  | * include additional rows if needed
131 |  |  |  |  | All other atypical expenditure projects or programmes |  |  | 0
132 |  |  |  | Atypical expenditure |  |  |  |  | 0
133
134 |  |  |  | Non-network assets expenditure |  |  |  |  | 1268.2665 | to row 18

## S6b.Actual Expenditure Opex
|  |  |  | Company Name | Alpine Energy Limitied
|  |  |  | For Year Ended | 2014-03-31
SCHEDULE 6b: REPORT ON OPERATIONAL EXPENDITURE FOR THE DISCLOSURE YEAR
This schedule requires a breakdown of operating expenditure incurred in the disclosure year. EDBs must provide explanatory comment on their operational expenditure in Schedule 14 (Explanatory notes to templates). This includes explanatory comment on any atypical operating expenditure and assets replaced or renewed as part of asset replacement and renewal operational expenditure, and additional information on insurance. This information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 6b(i): Operational Expenditure |  |  |  | ($000) | ($000)
8 |  |  | Service interruptions and emergencies |  | 1978.7777 |  | to S7
9 |  |  | Vegetation management |  | 110.4575 |  | to S7
10 |  |  | Routine and corrective maintenance and inspection |  | 3231.8705 |  | to S7
11 |  |  | Asset replacement and renewal |  | 571.7288 |  | to S7
12 |  |  | Network opex |  |  | 5892.8345
13 |  |  | System operations and network support |  | 4977.9269 |  | to S7
14 |  |  | Business support |  | 4400.799 |  | to S7
15 |  |  | Non-network opex |  |  | 9378.7259
16
17 |  | Operational expenditure |  |  |  | 15271.5604 | to S3
18 | 6b(ii): Subcomponents of Operational Expenditure (where known)
19 |  |  | Energy efficiency and demand side management, reduction of energy losses |  |  | 0 | to S7
20 |  |  | Direct billing* |  |  | N/A | to S7
21 |  |  | Research and development |  |  | 0 | to S7
22 |  |  | Insurance |  |  | 199.247 | to S7
23 | * Direct billing expenditure by suppliers that directly bill the majority of their consumers

## S7.Actual vs Forecast
[5 empty] | Company Name | Alpine Energy Limitied
[5 empty] | For Year Ended | 2014-03-31
SCHEDULE 7: COMPARISON OF FORECASTS TO ACTUAL EXPENDITURE
This schedule compares actual revenue and expenditure to the previous forecasts that were made for the disclosure year. Accordingly, this schedule requires the forecast revenue and expenditure information from previous disclosures to be inserted. EDBs must provide explanatory comment on the variance between actual and target revenue and forecast expenditure in Schedule 14 (Mandatory Explanatory Notes). This information is part of the audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8. For the purpose of this audit, target revenue and forecast expenditures only need to be verified back to previous disclosures.
sch ref
7 | 7(i): Revenue |  |  |  |  | Target ($000) ¹ | Actual ($000) | % variance
8 |  |  | Line charge revenue |  |  | 43300 | 42362.3463 | -2.165% | from S8
9 | 7(ii): Expenditure on Assets |  |  |  |  | Forecast ($000) ² | Actual ($000) | % variance
10 |  |  | Consumer connection |  |  | 2703 | 3700.7889 | 36.91% | from S6a
11 |  |  | System growth |  |  | 9227.94 | 8775.3786 | -4.904% | from S6a
12 |  |  | Asset replacement and renewal |  |  | 3524 | 2688.1421 | -23.72% | from S6a
13 |  |  | Asset relocations |  |  | 0 | 264.9422 | 0% | from S6a
14 |  |  | Reliability, safety and environment:
15 |  |  |  | Quality of supply |  | 195.2448 | 86.4254 | -55.73% | from S6a
16 |  |  |  | Legislative and regulatory |  | 0 | 0 | 0% | from S6a
17 |  |  |  | Other reliability, safety and environment |  | 5645.2552 | 2498.8799 | -55.73% | from S6a
18 |  |  | Total reliability, safety and environment |  |  | 5840.5 | 2585.3053 | -55.73%
19 |  | Expenditure on network assets |  |  |  | 21295.44 | 18014.5569 | -15.41%
20 |  |  | Non-network capex |  |  | 1312 | 1268.2665 | -3.333% | from S6a
21 |  | Expenditure on assets |  |  |  | 22607.44 | 19282.8235 | -14.71%
22 | 7(iii): Operational Expenditure
23 |  |  | Service interruptions and emergencies |  |  | 1484.5232 | 1978.7777 | 33.29% | from S6b
24 |  |  | Vegetation management |  |  | 122.7706 | 110.4575 | -10.03% | from S6b
25 |  |  | Routine and corrective maintenance and inspection |  |  | 2946.495 | 3231.8705 | 9.685% | from S6b
26 |  |  | Asset replacement and renewal |  |  | 797.7737 | 571.7288 | -28.33% | from S6b
27 |  | Network opex |  |  |  | 5351.5624 | 5892.8345 | 10.11%
28 |  |  | System operations and network support |  |  | 4057.4162 | 4977.9269 | 22.69% | from S6b
29 |  |  | Business support |  |  | 5083.1408 | 4400.799 | -13.42% | from S6b
30 |  | Non-network opex |  |  |  | 9140.557 | 9378.7259 | 2.606%
31 |  | Operational expenditure |  |  |  | 14492.1195 | 15271.5604 | 5.378%
32 | 7(iv): Subcomponents of Expenditure on Assets (where known)
33 |  |  | Energy efficiency and demand side management, reduction of energy losses |  |  | 0 | 11.6526 | 0% | from S6a
34 |  |  | Overhead to underground conversion |  |  | 0 | 236.1932 | 0% | from S6a
35 |  |  | Research and development |  |  | 0 | 74 | 0% | from S6a
36
37 | 7(v): Subcomponents of Operational Expenditure (where known)
38 |  |  | Energy efficiency and demand side management, reduction of energy losses |  |  | n/a | 0 | 0% | from S6b
39 |  |  | Direct billing |  |  | n/a | N/A | 0% | from S6b
40 |  |  | Research and development |  |  | n/a | 0 | 0% | from S6b
41 |  |  | Insurance |  |  | 175.2 | 199.247 | 13.73% | from S6b
42
43 | 1 From the nominal dollar target revenue for the disclosure year disclosed under clause 2.4.3(3) of the Determination
44 | 2 From the nominal dollar expenditure forecast and disclosed in the second to last AMP as the year CY+1 forecast

## S8.Billed Quantities+Revenues
[15 empty] | Company Name | Alpine Energy Limitied
[15 empty] | For Year Ended | 2014-03-31
Network / Sub-Network Name
SCHEDULE 8: REPORT ON BILLED QUANTITIES AND LINE CHARGE REVENUES
This schedule requires the billed quantities and associated line charge revenues for each price category code used by the EDB in its pricing schedules. Information is also required on the number of ICPs that are included in each consumer group or price category code, and the energy delivered to these ICPs.
sch ref
8 | 8(i): Billed Quantities by Price Component
9
10
11 | [9 empty] | Billed quantities by price component | [7 empty] | Add extra columns for additional billed quantities by price component as necessary
12 | [7 empty] | Price component |  | Distribution fixed | Distribution variable day | Distribution variable night | Distribution demand | Transmission Fixed | Transmission Variable day | Transmission Variable night | Transmission demand
13 |  | Consumer group name or price category code | Consumer type or types (eg, residential, commercial etc.) | Standard or non-standard consumer group (specify) | Average no. of ICPs in disclosure year | Energy delivered to ICPs in disclosure year (MWh) |  | Unit charging basis (eg, days, kW of demand, kVA of capacity, etc.) |  | $/annum | $/kWh | $/kWh | $/(kWh*annum) | $/annum | $/kWh | $/kWh | $/(kWh*annum)
14
15 |  | LOWHCA | Low Charge | Standard | 1017 | 5999.7297 |  |  |  | 1017 | 4370782.5601 | 1628947.1259 | 0 | 1017 | 4370782.5601 | 1628947.1259 | 0
16 |  | LOWLCA | Low Charge | Standard | 6598 | 38924.5 |  |  |  | 6598 | 28356365.1247 | 10568134.8442 | 0 | 6598 | 28356365.1247 | 10568134.8442 | 0
17 |  | LOWUHCA | Low Uncontrolled | Standard | 5 | 29.4972 |  |  |  | 5 | 21488.6065 | 8008.5896 | 0 | 5 | 21488.6065 | 8008.5896 | 0
|  | LOWULCA | Low Uncontrolled | Standard | 14 | 82.5921 |  |  |  | 14 | 60168.0982 | 22424.0509 | 0 | 14 | 60168.0982 | 22424.0509 | 0
|  | 015HCA | 015 | Standard | 6190 | 58580.2257 |  |  |  | 6190 | 42675494.0883 | 15904731.5861 | 0 | 6190 | 42675494.0883 | 15904731.5861 | 0
|  | 015LCA | 015 | Standard | 14733 | 134684.0964 |  |  |  | 14733 | 98116903.6822 | 36567192.7289 | 0 | 14733 | 98116903.6822 | 36567192.7289 | 0
|  | 015UHCA | 015 Uncontrolled | Standard | 36 | 28.4724 |  |  |  | 36 | 20742.0161 | 7730.3428 | 0 | 36 | 20742.0161 | 7730.3428 | 0
|  | 015ULCA | 015 Uncontrolled | Standard | 55 | 2.5898 |  |  |  | 55 | 1886.6492 | 703.1354 | 0 | 55 | 1886.6492 | 703.1354 | 0
|  | 360HCA | 360 | Standard | 435 | 10349.8395 |  |  |  | 435 | 7539822.679 | 2810016.8136 | 0 | 435 | 7539822.679 | 2810016.8136 | 0
|  | 360LCA | 360 | Standard | 681 | 16202.8522 |  |  |  | 681 | 11803722.4009 | 4399129.7703 | 0 | 681 | 11803722.4009 | 4399129.7703 | 0
|  | 360UHCA | 360 Uncontrolled | Standard | 13 | 309.3055 |  |  |  | 13 | 225328.0341 | 83977.514 | 0 | 13 | 225328.0341 | 83977.514 | 0
|  | 360ULCA | 360 Uncontrolled | Standard | 7 | 166.5491 |  |  |  | 7 | 121330.4799 | 45218.6614 | 0 | 7 | 121330.4799 | 45218.6614 | 0
18 |  | ASSHCA | Assessed | Standard | 1125 | 93900.94 |  |  |  | 1125 | 68406513.6977 | 25494426.306 | 86993 | 1125 | 68406513.6977 | 25494426.306 | 86993
19 |  | ASSLCA | Assessed | Standard | 353 | 24747.6258 |  |  |  | 353 | 18028560.7664 | 6719065.0278 | 34215 | 353 | 18028560.7664 | 6719065.0278 | 34215
20 |  | TOU400HCA | TOU 400V | Standard | 33 | 16095.5549 |  |  |  | 33 | 11468210.42 | 4627344.45 | 6118 | 33 | 11468210.42 | 4627344.45 | 6118
21 |  | TOU400LCA | TOU 400V | Standard | 104 | 91045.7165 |  |  |  | 104 | 62775647.94 | 28270068.6 | 22495 | 104 | 62775647.94 | 28270068.6 | 22495
22 |  | TOU11HCA | TOU 11kV | Standard | 6 | 23601.2954 |  |  |  | 6 | 17189719.21 | 6411576.15 | 5801 | 6 | 17189719.21 | 6411576.15 | 5801
23 |  | TOU11LCA | TOU 11kV | Standard | 4 | 16664.1012 |  |  |  | 4 | 11585963.87 | 5078137.38 | 4065 | 4 | 11585963.87 | 5078137.38 | 4065
24 |  | IND | IND | Non-standard | 4 | 184478.3392 |  |  |  | 4 | 128159383.82 | 56318955.36 | 0 | 4 | 128159383.82 | 56318955.36 | 0
25 |  | Add extra rows for additional consumer groups or price category codes as necessary
26 |  |  |  | Standard consumer totals | 31409 | 531415.4834 |  |  |  | 31409 | 382768650.3233 | 148646833.0767 | 159687 | 31409 | 382768650.3233 | 148646833.0767 | 159687
27 |  |  |  | Non-standard consumer totals | 4 | 184478.3392 |  |  |  | 4 | 128159383.82 | 56318955.36 | 0 | 4 | 128159383.82 | 56318955.36 | 0
28 |  |  |  | Total for all consumers | 31413 | 715893.8226 |  |  |  | 31413 | 510928034.1433 | 204965788.4367 | 159687 | 31413 | 510928034.1433 | 204965788.4367 | 159687 |  | to S9e
29
38 | 8(ii): Line Charge Revenues ($000) by Price Component
39
40 | [9 empty] | Line charge revenues ($000) by price component | [7 empty] | Add extra columns for additional line charge revenues by price component as necessary
41 | [7 empty] | Total transmission line charge revenue (if available) | Price component | Distribution fixed | Distribution variable day | Distribution variable night | Distribution demand | Transmission Fixed | Transmission Variable day | Transmission Variable night | Transmission demand
42 |  | Consumer group name or price category code | Consumer type or types (eg, residential, commercial etc.) | Standard or non-standard consumer group (specify) | Total line charge revenue in disclosure year | Notional revenue foregone (if applicable) | Total distribution line charge revenue |  | Rate (eg, $/day, $/kWh, etc.) | $/annum | $/kWh | $/kWh | $/(kWh*annum) | $/annum | $/kWh | $/kWh | $/(kWh*annum)
43
44 |  | LOWHCA | Low Charge | Standard | 513638.248 | N/A | 413391.0989 | 100247.1491 |  | 47390.2242 | 297066.0239 | 68934.8508 | 0 | 0 | 93161.3706 | 7085.7785 | 0
45 |  | LOWLCA | Low Charge | Standard | 3091074.1364 | N/A | 2440699.8102 | 650374.3262 |  | 307453.9819 | 1751519.8537 | 381725.9746 | 0 | 0 | 604403.8573 | 45970.4689 | 0
|  | LOWUHCA | Low Uncontrolled | Standard | 3503.6274 | N/A | 2032.4046 | 1471.2228 |  | 232.9903 | 1460.5016 | 338.9127 | 0 | 0 | 1170.7565 | 300.4663 | 0
|  | LOWULCA | Low Uncontrolled | Standard | 9298.2351 | N/A | 5178.8114 | 4119.4237 |  | 652.3728 | 3716.4713 | 809.9672 | 0 | 0 | 3278.1182 | 841.3056 | 0
|  | 015HCA | 015 | Standard | 4629602.9376 | N/A | 3650847.7345 | 978755.2031 |  | 1999229.4173 | 1500354.2708 | 151264.0464 | 0 | 0 | 909573.7582 | 69181.4449 | 0
|  | 015LCA | 015 | Standard | 10052710.6131 | N/A | 7802416.1046 | 2250294.5085 |  | 4005115.5975 | 3449523.4003 | 347777.1069 | 0 | 0 | 2091236.7328 | 159057.7757 | 0
|  | 015UHCA | 015 Uncontrolled | Standard | 22331.8461 | N/A | 12429.9357 | 9901.9104 |  | 11627.1824 | 729.2329 | 73.5204 | 0 | 9426.1958 | 442.0896 | 33.625 | 0
|  | 015ULCA | 015 Uncontrolled | Standard | 29468.9808 | N/A | 15024.5784 | 14444.4025 |  | 14951.5617 | 66.3295 | 6.6873 | 0 | 14401.1325 | 40.2115 | 3.0585 | 0
|  | 360HCA | 360 | Standard | 978499.3294 | N/A | 805574.7779 | 172924.5516 |  | 513770.0897 | 265079.6528 | 26725.0353 | 0 | 0 | 160701.7094 | 12222.8421 | 0
|  | 360LCA | 360 | Standard | 1415663.1125 | N/A | 1144946.7456 | 270716.3669 |  | 688121.4751 | 414986.7668 | 41838.5036 | 0 | 0 | 251581.2968 | 19135.0701 | 0
|  | 360UHCA | 360 Uncontrolled | Standard | 32646.4127 | N/A | 24074.6485 | 8571.7642 |  | 15354.0487 | 7921.9207 | 798.6792 | 0 | 3403.904 | 4802.5798 | 365.2803 | 0
46 |  | 360ULCA | 360 Uncontrolled | Standard | 16384.4746 | N/A | 11768.9093 | 4615.5653 |  | 7073.2017 | 4265.6496 | 430.058 | 0 | 1832.8714 | 2586.0045 | 196.6894 | 0
47 |  | ASSHCA | Assessed | Standard | 8648608.2558 | N/A | 3783755.8435 | 4864852.4122 |  | 120938.2049 | 2404986.9174 | 242468.1021 | 1015362.619 | 0 | 1457997.642 | 110894.1223 | 3295960.648
48 |  | ASSLCA | Assessed | Standard | 2755685.8292 | N/A | 1071065.0441 | 1684620.7851 |  | 32402.8331 | 633835.1487 | 63902.5537 | 340924.5087 | 0 | 384255.7918 | 29226.185 | 1271138.8083
49 |  | TOU400HCA | TOU 400V | Standard | 995473.3609 | N/A | 513119.7227 | 482353.6382 |  | 3549.4417 | 154413.6045 | 9395.1732 | 345761.5032 | 0 | 39906.9856 | 9560.6787 | 432885.974
50 |  | TOU400LCA | TOU 400V | Standard | 3874655.8978 | N/A | 2006141.1351 | 1868514.7627 |  | 9624.1391 | 845242.0838 | 57398.4053 | 1093876.507 | 0 | 218446.1904 | 58409.536 | 1591659.0363
51 |  | TOU11HCA | TOU 11kV | Standard | 974532.6659 | N/A | 491012.6112 | 483520.0547 |  | 645.353 | 231450.8024 | 13017.8052 | 245898.6506 | 0 | 59816.6454 | 13247.127 | 410456.2823
52 |  | TOU11LCA | TOU 11kV | Standard | 653365.3765 | N/A | 314932.9107 | 338432.4659 |  | 370.1592 | 155999.0946 | 10310.445 | 148253.2119 | 0 | 40316.7431 | 10492.0739 | 287623.6489
53 |  | IND | IND | Non-standard | 3665202.92 | N/A | 2408146.62 | 1257056.3 |  | 2408146.62 | 0 | 0 | 0 | 1257056.3 | 0 | 0 | 0
54 |  | Add extra rows for additional consumer groups or price category codes as necessary
55 |  |  |  | Standard consumer totals | 38697143.34 | 0 | 24508412.8269 | 14188730.5131 |  | 7778502.2743 | 12122617.7252 | 1417215.8269 | 3190077.0004 | 29064.1038 | 6323718.4835 | 546223.528 | 7289724.3978
56 |  |  |  | Non-standard consumer totals | 3665202.92 | 0 | 2408146.62 | 1257056.3 |  | 2408146.62 | 0 | 0 | 0 | 1257056.3 | 0 | 0 | 0
57 |  |  |  | Total for all consumers | 42362346.26 | 0 | 26916559.4469 | 15445786.8131 |  | 10186648.8943 | 12122617.7252 | 1417215.8269 | 3190077.0004 | 1286120.4038 | 6323718.4835 | 546223.528 | 7289724.3978 |  | to S3 & S7
58
59 | 8(iii): Number of ICPs directly billed | [5 empty] | Check | OK
60 |  | Number of directly billed ICPs at year end |  | 4

## S9a.Asset Register
[5 empty] | Company Name | Alpine Energy Limitied
[5 empty] | For Year Ended | 2014-03-31
Network / Sub-network Name
SCHEDULE 9a: ASSET REGISTER
This schedule requires a summary of the quantity of assets that make up the network, by asset category and asset class. All units relating to cable and line assets, that are expressed in km, refer to circuit lengths.
sch ref
8 | Voltage | Asset category | Asset class | Units | Items at start of year (quantity) | Items at end of year (quantity) | Net change | Data accuracy 1–4
9 | All | Overhead Line | Concrete poles / steel structure | No. | 25858 | 25936 | 78 | 2
10 | All | Overhead Line | Wood poles | No. | 20388 | 20444 | 56 | 2
11 | All | Overhead Line | Other pole types | No. | 674 | 675 | 1 | 2
12 | HV | Subtransmission Line | Subtransmission OH up to 66kV conductor | km | 217.5135 | 217.5136 | 0.00010046 | 2
13 | HV | Subtransmission Line | Subtransmission OH 110kV+ conductor | km | 0.016791 | 0.016791 | 0 | 3
14 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (XLPE) | km | 26.8735 | 26.8735 | 0 | 3
15 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Oil pressurised) | km | 0 | 0 | 0 | 4
16 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Gas pressurised) | km | 0 | 0 | 0 | 4
17 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (PILC) | km | 0 | 0 | 0 | 4
18 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (XLPE) | km | 0 | 0 | 0 | 4
19 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Oil pressurised) | km | 0 | 0 | 0 | 4
20 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Gas Pressurised) | km | 0 | 0 | 0 | 4
21 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (PILC) | km | 0 | 0 | 0 | 4
22 | HV | Subtransmission Cable | Subtransmission submarine cable | km | 0 | 0 | 0 | 4
23 | HV | Zone substation Buildings | Zone substations up to 66kV | No. | 0 | 0 | 0 | 4
24 | HV | Zone substation Buildings | Zone substations 110kV+ | No. | 0 | 0 | 0 | 4
25 | HV | Zone substation switchgear | 50/66/110kV CB (Indoor) | No. | 0 | 0 | 0 | 4
26 | HV | Zone substation switchgear | 50/66/110kV CB (Outdoor) | No. | 1 | 1 | 0 | 4
27 | HV | Zone substation switchgear | 33kV Switch (Ground Mounted) | No. | 29 | 29 | 0 | 2
28 | HV | Zone substation switchgear | 33kV Switch (Pole Mounted) | No. | 40 | 40 | 0 | 2
29 | HV | Zone substation switchgear | 33kV RMU | No. | 0 | 0 | 0 | 4
30 | HV | Zone substation switchgear | 22/33kV CB (Indoor) | No. | 0 | 0 | 0 | 2
31 | HV | Zone substation switchgear | 22/33kV CB (Outdoor) | No. | 11 | 11 | 0 | 2
32 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (ground mounted) | No. | 0 | 0 | 0 | N/A
33 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (pole mounted) | No. | 0 | 0 | 0 | N/A
34 | HV | Zone Substation Transformer | Zone Substation Transformers | No. | 22 | 22 | 0 | 2
35 | HV | Distribution Line | Distribution OH Open Wire Conductor | km | 2894.4365 | 2907.2587 | 12.8222 | 2
36 | HV | Distribution Line | Distribution OH Aerial Cable Conductor | km | 0.32395 | 0.37211 | 0.048163 | 2
37 | HV | Distribution Line | SWER conductor | km | 6.7699 | 6.7699 | 0 | 3
38 | HV | Distribution Cable | Distribution UG XLPE or PVC | km | 114.7567 | 121.1709 | 6.4142 | 2
39 | HV | Distribution Cable | Distribution UG PILC | km | 129.4478 | 129.4406 | -0.0071671 | 2
40 | HV | Distribution Cable | Distribution Submarine Cable | km | 0 | 0 | 0 | 4
41 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (pole mounted) - reclosers and sectionalisers | No. | 218 | 221 | 3 | 2
42 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (Indoor) | No. | 38 | 42 | 4 | 2
43 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switches and fuses (pole mounted) | No. | 1318 | 1369 | 51 | 2
44 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switch (ground mounted) - except RMU | No. | 86 | 85 | -1 | 2
45 | HV | Distribution switchgear | 3.3/6.6/11/22kV RMU | No. | 476 | 481 | 5 | 2
46 | HV | Distribution Transformer | Pole Mounted Transformer | No. | 4750 | 4831 | 81 | 2
47 | HV | Distribution Transformer | Ground Mounted Transformer | No. | 863 | 886 | 23 | 2
48 | HV | Distribution Transformer | Voltage regulators | No. | 30 | 31 | 1 | 2
49 | HV | Distribution Substations | Ground Mounted Substation Housing | No. | 0 | 0 | 0 | N/A
50 | LV | LV Line | LV OH Conductor | km | 2894.5918 | 2907.4621 | 12.8703 | 2
51 | LV | LV Cable | LV UG Cable | km | 307.6149 | 314.016 | 6.4011 | 2
52 | LV | LV Street lighting | LV OH/UG Streetlight circuit | km | 0 | 0 | 0 | 4
53 | LV | Connections | OH/UG consumer service connections | No. | 31401 | 31643 | 242 | 4
54 | All | Protection | Protection relays (electromechanical, solid state and numeric) | No. | 0 | 0 | 0 | N/A
55 | All | SCADA and communications | SCADA and communications equipment operating as a single system | Lot | 1 | 1 | 0 | 1
56 | All | Capacitor Banks | Capacitors including controls | No | 17 | 16 | -1 | 2
57 | All | Load Control | Centralised plant | Lot | 6 | 6 | 0 | 4
58 | All | Load Control | Relays | No | 9169 | 9493 | 324 | 2
59 | All | Civils | Cable Tunnels | km | 0 | 0 | 0 | 2

## S9b.Asset Age Profile
[28 empty] | Company Name | Alpine Energy Limitied
[28 empty] | For Year Ended | 2014-03-31
Network / Sub-network Name
SCHEDULE 9b: ASSET AGE PROFILE
This schedule requires a summary of the age profile (based on year of installation) of the assets that make up the network, by asset category and asset class. All units relating to cable and line assets, that are expressed in km, refer to circuit lengths.
sch ref
|  | Disclosure Year (year ended) | 2014-03-31 |  | Number of assets at disclosure year end by installation date
9 | Voltage | Asset category | Asset class | Units | pre-1940 | 1940 –1949 | 1950 –1959 | 1960 –1969 | 1970 –1979 | 1980 –1989 | 1990 –1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | No. with Age unknown | Total assets at year end | No. with default dates | Data accuracy (1–4)
10 | All | Overhead Line | Concrete poles / steel structure | No. | 63 | 4 | 3518 | 6542 | 4574 | 2973 | 1839 | 198 | 195 | 304 | 520 | 550 | 916 | 360 | 347 | 291 | 325 | 201 | 85 | 347 | 487 | 248 |  |  |  | 1049 | 25936 | 0 | 3
11 | All | Overhead Line | Wood poles | No. | 12 | 7 | 3624 | 2142 | 2617 | 2017 | 2200 | 183 | 218 | 477 | 561 | 409 | 686 | 418 | 549 | 718 | 533 | 216 | 135 | 350 | 269 | 239 |  |  |  | 1864 | 20444 | 0 | 3
12 | All | Overhead Line | Other pole types | No. | 0 | 0 | 0 | 0 | 9 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 | 16 | 0 | 3
13 | HV | Subtransmission Line | Subtransmission OH up to 66kV conductor | km | 0 | 0 | 7.0813 | 44.2921 | 33.2817 | 11.5471 | 51.528 | 9.8032 | 0 | 10.1775 | 14.1576 | 5.0802 | 0.0069009 | 0.80549 | 0 | 0 | 0 | 1.1697 | 0.014299 | 0.12777 | 21.0941 | 7.3407 |  |  |  | 0.0059848 | 217.5136 | 0 | 3
14 | HV | Subtransmission Line | Subtransmission OH 110kV+ conductor | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016791 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0.016791 | 0 | 4
15 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (XLPE) | km | 0 | 0 | 0 | 0 | 0.034117 | 2.1794 | 2.2404 | 0 | 0 | 0 | 0.40119 | 0.49345 | 21.4407 | 0 | 0 | 0 | 0 | 0 | 0.062907 | 0.021377 | 0 | 0 |  |  |  | 0 | 26.8735 | 0 | 3
16 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Oil pressurised) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
17 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Gas pressurised) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
18 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (PILC) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
19 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (XLPE) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
20 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Oil pressurised) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
21 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Gas Pressurised) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
22 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (PILC) | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
23 | HV | Subtransmission Cable | Subtransmission submarine cable | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
24 | HV | Zone substation Buildings | Zone substations up to 66kV | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
25 | HV | Zone substation Buildings | Zone substations 110kV+ | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
26 | HV | Zone substation switchgear | 50/66/110kV CB (Indoor) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
27 | HV | Zone substation switchgear | 50/66/110kV CB (Outdoor) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 |  |  |  | 0 | 1 | 0 | 4
28 | HV | Zone substation switchgear | 33kV Switch (Ground Mounted) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
29 | HV | Zone substation switchgear | 33kV Switch (Pole Mounted) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 2
30 | HV | Zone substation switchgear | 33kV RMU | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
31 | HV | Zone substation switchgear | 22/33kV CB (Indoor) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
32 | HV | Zone substation switchgear | 22/33kV CB (Outdoor) | No. | 0 | 0 | 0 | 0 | 4 | 10 | 5 | 0 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 1 | 0 | 1 | 7 | 3 | 0 |  |  |  | 0 | 34 | 0 | 2
33 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (ground mounted) | No. | 0 | 0 | 10 | 19 | 4 | 29 | 14 | 1 | 4 | 2 | 2 | 1 | 18 | 16 | 10 | 6 | 13 | 5 | 8 | 23 | 9 | 7 |  |  |  | 0 | 201 | 0 | 2
34 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (pole mounted) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
45 | HV | Zone Substation Transformer | Zone Substation Transformers | No. | 0 | 0 | 2 | 3 | 7 | 3 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 |  |  |  | 0 | 20 | 4 | 3
46 | HV | Distribution Line | Distribution OH Open Wire Conductor | km | 6.2628 | 0 | 880.8092 | 519.675 | 360.132 | 255.1803 | 166.884 | 10.1757 | 21.9093 | 37.1396 | 83.2239 | 65.604 | 143.881 | 42.7661 | 54.9617 | 53.5173 | 58.0348 | 36.6155 | 17.1779 | 28.9711 | 37.524 | 26.1715 |  |  |  | 0.64191 | 2907.2587 | 0 | 3
47 | HV | Distribution Line | Distribution OH Aerial Cable Conductor | km | 0 | 0 | 0 | 0.13584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0023188 | 0.03147 | 0.049386 | 0 | 0.10493 | 0.048163 |  |  |  | 0 | 0.37211 | 0 | 2
48 | HV | Distribution Line | SWER conductor | km | 0 | 0 | 0 | 0 | 6.7699 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 6.7699 | 0 | 3
49 | HV | Distribution Cable | Distribution UG XLPE or PVC | km | 0 | 0 | 0 | 0.59013 | 1.1126 | 3.7389 | 3.2589 | 0.56016 | 1.7119 | 4.2249 | 4.2356 | 2.0004 | 4.2408 | 10.1775 | 6.775 | 15.9746 | 11.4584 | 9.1912 | 10.3653 | 16.0289 | 8.6491 | 6.4142 |  |  |  | 0.46221 | 121.1709 | 0 | 2
50 | HV | Distribution Cable | Distribution UG PILC | km | 0 | 0 | 0 | 9.5502 | 37.7456 | 54.0669 | 25.0798 | 1.4479 | 0.43921 | 0.0028 | 0.39615 | 0 | 0.036001 | 0.0080995 | 0.038453 | 0 | 0.11996 | 0.17844 | 0 | 0.29331 | 0 | 0 |  |  |  | 0.037934 | 129.4406 | 0 | 2
51 | HV | Distribution Cable | Distribution Submarine Cable | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
52 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (pole mounted) - reclosers and sectionalisers | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
53 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (Indoor) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
54 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switches and fuses (pole mounted) | No. | 12 | 1 | 814 | 882 | 783 | 611 | 540 | 53 | 73 | 112 | 202 | 177 | 245 | 167 | 200 | 301 | 285 | 251 | 186 | 283 | 275 | 224 |  |  |  | 97 | 6774 | 0 | 3
55 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switch (ground mounted) - except RMU | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 1
56 | HV | Distribution switchgear | 3.3/6.6/11/22kV RMU | No. | 0 | 0 | 0 | 16 | 57 | 50 | 41 | 6 | 6 | 10 | 9 | 8 | 11 | 6 | 6 | 5 | 8 | 16 | 6 | 8 | 4 | 5 |  |  |  | 4 | 282 | 0 | 3
57 | HV | Distribution Transformer | Pole Mounted Transformer | No. | 4 | 1 | 692 | 707 | 642 | 512 | 431 | 47 | 61 | 80 | 152 | 105 | 176 | 115 | 148 | 170 | 184 | 132 | 103 | 128 | 137 | 114 |  |  |  | 0 | 4841 | 6 | 2
58 | HV | Distribution Transformer | Ground Mounted Transformer | No. | 0 | 0 | 7 | 29 | 145 | 139 | 101 | 11 | 17 | 26 | 36 | 26 | 44 | 37 | 38 | 42 | 42 | 26 | 23 | 22 | 27 | 26 |  |  |  | 0 | 864 | 29 | 2
59 | HV | Distribution Transformer | Voltage regulators | No. | 0 | 0 | 1 | 1 | 0 | 1 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 11 | 3 | 1 | 1 | 1 |  |  |  | 0 | 31 | 0 | 3
60 | HV | Distribution Substations | Ground Mounted Substation Housing | No. | 0 | 0 | 7 | 29 | 145 | 139 | 101 | 11 | 17 | 26 | 36 | 26 | 44 | 37 | 38 | 42 | 42 | 26 | 23 | 22 | 27 | 26 |  |  |  | 0 | 864 | 29 | 1
61 | LV | LV Line | LV OH Conductor | km | 6.2628 | 0 | 880.8092 | 519.8108 | 360.132 | 255.1803 | 166.884 | 10.1757 | 21.9093 | 37.1396 | 83.2239 | 65.604 | 143.881 | 42.7661 | 54.9617 | 53.5173 | 58.0371 | 36.6469 | 17.2273 | 28.8024 | 37.6289 | 26.2196 |  |  |  | 0.64191 | 2907.4621 | 0 | 3
62 | LV | LV Cable | LV UG Cable | km | 0 | 0 | 0.79059 | 10.2591 | 48.3218 | 64.46 | 38.3218 | 4.0952 | 4.6304 | 11.0601 | 11.3811 | 5.5354 | 9.9287 | 19.6361 | 13.9663 | 17.9905 | 11.7765 | 9.7277 | 4.7348 | 11.8068 | 8.6149 | 6.4227 |  |  |  | 0.5554 | 314.016 | 0 | 3
63 | LV | LV Street lighting | LV OH/UG Streetlight circuit | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 4
64 | LV | Connections | OH/UG consumer service connections | No. | 2845 | 996 | 2897 | 4511 | 5790 | 3755 | 5663 | 542 | 180 | 284 | 301 | 335 | 436 | 453 | 415 | 415 | 530 | 365 | 263 | 313 | 340 | 329 |  |  |  | 0 | 31958 | 0 | 4
65 | All | Protection | Protection relays (electromechanical, solid state and numeric) | No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | N/A
66 | All | SCADA and communications | SCADA and communications equipment operating as a single system | Lot | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 1 | 1 | 0 | 1
67 | All | Capacitor Banks | Capacitors including controls | No | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 6 | 0 | 1 | 0 | 0 |  |  |  | 4 | 16 | 0 | 3
68 | All | Load Control | Centralised plant | Lot | 0 | 0 | 0 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 |  |  |  | 0 | 6 | 0 | 3
69 | All | Load Control | Relays | No | 56 | 21 | 45 | 190 | 367 | 184 | 390 | 222 | 40 | 115 | 127 | 136 | 152 | 116 | 91 | 116 | 1278 | 134 | 232 | 478 | 1323 | 10431 |  |  |  | 0 | 16244 | 1496 | 2
70 | All | Civils | Cable Tunnels | km | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 3

## S9c.Overhead Lines
|  |  | Company Name | Alpine Energy Limitied
|  |  | For Year Ended | 2014-03-31
Network / Sub-network Name
SCHEDULE 9c: REPORT ON OVERHEAD LINES AND UNDERGROUND CABLES
This schedule requires a summary of the key characteristics of the overhead line and underground cable network. All units relating to cable and line assets, that are expressed in km, refer to circuit lengths.
sch ref
9
10 | Circuit length by operating voltage (at year end) |  |  | Overhead (km) | Underground (km) | Total circuit length (km)
11 |  | > 66kV |  | 0 | 0 | 0
12 |  | 50kV & 66kV |  | 0 | 0 | 0
13 |  | 33kV |  | 218 | 27 | 245
14 |  | SWER (all SWER voltages) |  | 0 | 7 | 7
15 |  | 22kV (other than SWER) |  | 144 | 1 | 145
16 |  | 6.6kV to 11kV (inclusive—other than SWER) |  | 2763 | 316 | 3079
17 |  | Low voltage (< 1kV) |  | 375 | 294 | 669
18 | Total circuit length (for supply) |  |  | 3500 | 645 | 4145 | to S1
19
20 |  | Dedicated street lighting circuit length (km) |  | 0 | 0 | 0
21 |  | Circuit in sensitive areas (conservation areas, iwi territory etc) (km) |  |  |  | 38
22
23 | Overhead circuit length by terrain (at year end) |  |  | Circuit length (km) | (% of total overhead length)
24 |  | Urban |  | 315 | 9%
25 |  | Rural |  | 3089 | 88.26%
26 |  | Remote only |  | 0 | 0%
27 |  | Rugged only |  | 96 | 2.743%
28 |  | Remote and rugged |  | 0 | 0%
29 |  | Unallocated overhead lines |  | 0 | 0% |  |  | Test for cell G30 conditional formatting
30 | Total overhead length |  |  | 3500 | 100% |  |  | Cell G18 | Agrees with cell Q17 value
31 | [7 empty] | 3500 | TRUE
32 |  |  |  | Circuit length (km) | (% of total circuit length)
33 |  | Length of circuit within 10km of coastline or geothermal areas (where known) |  | 1661 | 40.07%
34 |  |  |  | Circuit length (km) | (% of total overhead length)
35 |  | Overhead circuit requiring vegetation management |  | 0 | 0%

## S9d.Embedded Networks
|  |  | Company Name | Alpine Energy Limitied
|  |  | For Year Ended | 2014-03-31
SCHEDULE 9d: REPORT ON EMBEDDED NETWORKS
This schedule requires information concerning embedded networks owned by an EDB that are embedded in another EDB’s network or in another embedded network.
sch ref
8 |  | Location * |  | Number of ICPs served | Line charge revenue ($000)
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26 | * Extend embedded distribution networks table as necessary to disclose each embedded network owned by the EDB which is embedded in another EDB’s network or in another embedded network

## S9e.Demand
[5 empty] | Company Name | Alpine Energy Limitied
[5 empty] | For Year Ended | 2014-03-31
Network / Sub-network Name
SCHEDULE 9e: REPORT ON NETWORK DEMAND
This schedule requires a summary of the key measures of network utilisation for the disclosure year (number of new connections including distributed generation, peak demand and electricity volumes conveyed).
sch ref
8 | 9e(i): Consumer Connections
9 |  |  | Number of ICPs connected in year by consumer type
10 |  |  |  | Consumer types defined by EDB* |  |  | Number of connections (ICPs)
11 |  |  |  | Low Charge |  |  | -
|  |  |  | Low Uncontrolled |  |  | -
|  |  |  | 015 |  |  | 316
|  |  |  | 015 Uncontrolled |  |  | -
|  |  |  | 360 |  |  | 49
|  |  |  | 360 Uncontrolled |  |  | -
12 |  |  |  | Assessed |  |  | 39
13 |  |  |  | TOU 400V |  |  | 1
14 |  |  |  | TOU 11kV |  |  | -
15 |  |  |  | IND |  |  | -
16 |  |  |  | * include additional rows if needed
17 |  |  | Connections total |  |  |  | 405
18
19 |  | Distributed generation
20 |  |  |  | Number of connections made in year |  |  | 27 | connections
21 |  |  |  | Capacity of distributed generation installed in year |  |  | 0.12 | MVA
22 | 9e(ii): System Demand
23
24 | [6 empty] | Demand at time of maximum coincident demand (MW)
25 |  | Maximum coincident system demand
26 |  |  |  | GXP demand |  |  | 120.446
27 |  | plus |  | Distributed generation output at HV and above |  |  | 6.6637
28 |  |  | Maximum coincident system demand |  |  |  | 127.1097
29 |  | less |  | Net transfers to (from) other EDBs at HV and above |  |  | 0
30 |  |  | Demand on system for supply to consumers' connection points |  |  |  | 127.1097
31 |  | Electricity volumes carried |  |  |  |  | Energy (GWh) | Energy (GWh)
32 |  |  |  | Electricity supplied from GXPs |  |  | 737.9371
33 |  | less |  | Electricity exports to GXPs |  |  | 19.4998
34 |  | plus |  | Electricity supplied from distributed generation |  |  | 33.6391
35 |  | less |  | Net electricity supplied to (from) other EDBs |  |  | 0
36 |  |  | Electricity entering system for supply to consumers' connection points |  |  |  | 752.0764
37 |  | less |  | Total energy delivered to ICPs |  |  | 715.8938 |  | from S8
38 |  |  | Electricity losses (loss ratio) |  |  |  | 36.1826 | 4.811%
39
40 |  |  | Load factor |  |  |  | 0.67543
41 | 9e(iii): Transformer Capacity
42 | [6 empty] | (MVA)
43 |  |  |  | Distribution transformer capacity (EDB owned) |  |  | 416.0145 |  | to S1
44 |  |  |  | Distribution transformer capacity (Non-EDB owned) |  |  | 86.7
45 |  |  | Total distribution transformer capacity |  |  |  | 502.7145
46
47 |  |  | Zone substation transformer capacity |  |  |  | 300

## S10.Reliability
[6 empty] | Company Name | Alpine Energy Limitied
[6 empty] | For Year Ended | 2014-03-31
Network / Sub-network Name
SCHEDULE 10: REPORT ON NETWORK RELIABILITY
This schedule requires a summary of the key measures of network reliability (interruptions, SAIDI, SAIFI and fault rate) for the disclosure year. EDBs must provide explanatory comment on their network reliability for the disclosure year in Schedule 14 (Explanatory notes to templates). The SAIFI and SAIDI information is part of audited disclosure information (as defined in section 1.4 of the ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
8 | 10(i): Interruptions
9 |  | Interruptions by class |  |  | Number of interruptions
10 |  |  |  | Class A (planned interruptions by Transpower) | 2
11 |  |  |  | Class B (planned interruptions on the network) | 160
12 |  |  |  | Class C (unplanned interruptions on the network) | 248
13 |  |  |  | Class D (unplanned interruptions by Transpower) | 8
14 |  |  |  | Class E (unplanned interruptions of EDB owned generation) | 0
15 |  |  |  | Class F (unplanned interruptions of generation owned by others) | 0
16 |  |  |  | Class G (unplanned interruptions caused by another disclosing entity) | 0
17 |  |  |  | Class H (planned interruptions caused by another disclosing entity) | 0
18 |  |  |  | Class I (interruptions caused by parties not included above) | 0
19 |  |  | Total |  | 418
20
21 |  | Interruption restoration |  |  | ≤3Hrs | >3hrs
22 |  |  |  | Class C interruptions restored within | 118 | 130
23
24 |  | SAIFI and SAIDI by class |  |  | SAIFI | SAIDI
25 |  |  |  | Class A (planned interruptions by Transpower) | 0.047585 | 4.9186
26 |  |  |  | Class B (planned interruptions on the network) | 0.14863 | 33.9899
27 |  |  |  | Class C (unplanned interruptions on the network) | 2.0481 | 824.4071
28 |  |  |  | Class D (unplanned interruptions by Transpower) | 0.20509 | 11.9224
29 |  |  |  | Class E (unplanned interruptions of EDB owned generation) | 0 | 0
30 |  |  |  | Class F (unplanned interruptions of generation owned by others) | 0 | 0
31 |  |  |  | Class G (unplanned interruptions caused by another disclosing entity) | 0 | 0
32 |  |  |  | Class H (planned interruptions caused by another disclosing entity) | 0 | 0
33 |  |  |  | Class I (interruptions caused by parties not included above) | 0 | 0
34 |  |  | Total |  | 2.4494 | 875.2381
35
36 |  | Normalised SAIFI and SAIDI |  |  | Normalised SAIFI | Normalised SAIDI
37 |  |  |  | Classes B & C (interruptions on the network) | 1.999 | 274.7657
38
39 |  | Quality path normalised reliability limit |  |  | SAIFI reliability limit | SAIDI reliability limit
40 |  |  |  | SAIFI and SAIDI limits applicable to disclosure year* | 1.6937 | 164.2206
41 |  |  |  | * not applicable to exempt EDBs
42 | 10(ii): Class C Interruptions and Duration by Cause
43
44 |  | Cause |  |  | SAIFI | SAIDI
45 |  |  |  | Lightning | 0.042858 | 6.1367
46 |  |  |  | Vegetation | 0.086802 | 13.6156
47 |  |  |  | Adverse weather | 0.92283 | 695.0359
48 |  |  |  | Adverse environment | 0.0419 | 3.4587
49 |  |  |  | Third party interference | 0.32246 | 35.9982
50 |  |  |  | Wildlife | 0.081277 | 6.0163
51 |  |  |  | Human error | 0.0059721 | 0.27101
52 |  |  |  | Defective equipment | 0.47534 | 54.3445
53 |  |  |  | Cause unknown | 0.068695 | 9.5303
62 | 10(iii): Class B Interruptions and Duration by Main Equipment Involved
63
64 |  | Main equipment involved |  |  | SAIFI | SAIDI
65 |  |  |  | Subtransmission lines | 0 | 0
66 |  |  |  | Subtransmission cables | 0 | 0
67 |  |  |  | Subtransmission other | 0 | 0
68 |  |  |  | Distribution lines (excluding LV) | 0.14231 | 33.2945
69 |  |  |  | Distribution cables (excluding LV) | 0.003481 | 0.13662
70 |  |  |  | Distribution other (excluding LV) | 0.0028423 | 0.55875
71 | 10(iv): Class C Interruptions and Duration by Main Equipment Involved
72
73 |  | Main equipment involved |  |  | SAIFI | SAIDI
74 |  |  |  | Subtransmission lines | 0.28774 | 118.4636
75 |  |  |  | Subtransmission cables | 0 | 0
76 |  |  |  | Subtransmission other | 0 | 0
77 |  |  |  | Distribution lines (excluding LV) | 0.29244 | 702.0102
78 |  |  |  | Distribution cables (excluding LV) | 0.02424 | 3.9333
79 |  |  |  | Distribution other (excluding LV) | 0 | 0
80 | 10(v): Fault Rate
81 |  | Main equipment involved |  |  | Number of Faults | Circuit length (km) |  | Fault rate (faults per 100km)
82 |  |  |  | Subtransmission lines | 16 | 218 |  | 7.3394
83 |  |  |  | Subtransmission cables | 0 | 27 |  | 0
84 |  |  |  | Subtransmission other | 0
85 |  |  |  | Distribution lines (excluding LV) | 230 | 2907 |  | 7.9119
86 |  |  |  | Distribution cables (excluding LV) | 2 | 324 |  | 0.61728
87 |  |  |  | Distribution other (excluding LV) | 0
88 |  |  | Total |  | 248