## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Alpine Energy Limited
| Disclosure Date | 2025-08-31
| Disclosure Year (year ended) | 2025-03-31
Template for Schedule 10a
Prepared 16 February 2024.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Targeted Review 2024) Amendment Determination 2024 [2024] NZCC 2.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Alpine Energy Limited
[15 empty] | For Year Ended | 2025-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | JDJ060 | CB W465 |  | Otaio | 2024-04-02 04:37 | 45384.1924 | 2024-04-02 04:43 | 45384.1965 | 0.014857 | 0.0024761 | 84 | 504 | Planned | Planned interruption | Red tag pole replacement
10 |  | JDJ060 | CB W685 |  | Otaio | 2024-04-02 04:37 | 45384.1924 | 2024-04-02 04:42 | 45384.1958 | 0.0092855 | 0.0018571 | 63 | 315 | Planned | Planned interruption | Red tag pole replacement
11 |  | JDJ060 | ABS W306-CB W465-CB W685 |  | Otaio | 2024-04-02 04:39 | 45384.1937 | 2024-04-02 04:41 | 45384.1951 | 0.0076052 | 0.0038026 | 129 | 258 | Planned | Planned interruption | Red tag pole replacement
12 |  | JDJ060 | Links W571-ABS W306 |  | Otaio | 2024-04-02 11:00 | 45384.4583 | 2024-04-02 14:22 | 45384.5986 | 0.27391 | 0.001356 | 46 | 9292 | Planned | Planned interruption | Red tag pole replacement
13 |  | JDJ060 | CB W465 |  | Otaio | 2024-04-02 18:30 | 45384.7708 | 2024-04-02 18:35 | 45384.7743 | 0.012381 | 0.0024761 | 84 | 420 | Planned | Planned interruption | Red tag pole replacement
14 |  | JDJ060 | CB W685 |  | Otaio | 2024-04-02 18:31 | 45384.7715 | 2024-04-02 18:35 | 45384.7743 | 0.0074284 | 0.0018571 | 63 | 252 | Planned | Planned interruption | Red tag pole replacement
15 |  | JDJ060 | ABS W306-CB W465-CB W685 |  | Otaio | 2024-04-02 18:33 | 45384.7729 | 2024-04-02 18:34 | 45384.7736 | 0.0038026 | 0.0038026 | 129 | 129 | Planned | Planned interruption | Red tag pole replacement
16 |  | SKE1415 | TX A790 CCT2 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 18:03 | 45385.7521 | 0.48812 | 0.00085485 | 29 | 16559 | Planned | Planned interruption | TX Replacement
17 |  | SKE1415 | TX A790-TX A790 CCT2 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:56 | 45385.7472 | 0.49876 | 0.00088433 | 30 | 16920 | Planned | Planned interruption | TX Replacement
18 |  | SKE1415 | TX A789-TX A789 CCT2 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:47 | 45385.741 | 0.45808 | 0.00082537 | 28 | 15540 | Planned | Planned interruption | TX Replacement
19 |  | SKE1415 | TX A798 CCT2 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:38 | 45385.7347 | 0.64379 | 0.0011791 | 40 | 21840 | Planned | Planned interruption | TX Replacement
20 |  | SKE1415 | TX A546 CCT3 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:45 | 45385.7396 | 0.50534 | 0.00091381 | 31 | 17143 | Planned | Planned interruption | TX Replacement
21 |  | SKE1415 | TX A546 CCT2 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:43 | 45385.7382 | 0.24363 | 0.00044216 | 15 | 8265 | Planned | Planned interruption | TX Replacement
22 |  | SKE1415 | Pole 20795 Links W749-TX A546 CCT3-TX A546 CCT2-TX A790-TX789 |  | Waimate | 2024-04-03 08:32 | 45385.3556 | 2024-04-03 17:33 | 45385.7312 | 0.68574 | 0.0012675 | 43 | 23263 | Planned | Planned interruption | TX Replacement
23 |  | GWM1138 | Fuses L305 |  | Waipopo | 2024-04-03 09:00 | 45385.375 | 2024-04-03 10:14 | 45385.4264 | 0.034902 | 0.00047164 | 16 | 1184 | Planned | Planned interruption | Tree cutting
24 |  | JJV135 | Services 76, 76a & 80 Wai-iti Rd |  | Nile Street | 2024-04-03 09:00 | 45385.375 | 2024-04-03 15:52 | 45385.6611 | 0.036434 | 8.8433e-05 | 3 | 1236 | Planned | Planned interruption | Sub Maint
25 |  | JJV135 | DB Q43 |  | Nile Street | 2024-04-03 09:00 | 45385.375 | 2024-04-03 15:48 | 45385.6583 | 0.10824 | 0.0002653 | 9 | 3672 | Planned | Planned interruption | Sub Maint
26 |  | JJV135 | GRM CB5-RMU E14-DB Q43-Services 76, 76a & 80 Wai-iti Rd |  | Nile Street | 2024-04-03 09:00 | 45385.375 | 2024-04-03 15:35 | 45385.6493 | 1.9212 | 0.0048638 | 165 | 65175 | Planned | Planned interruption | Sub Maint
27 |  | JDJ074 | TX D1064 |  | Winchester | 2024-04-03 09:48 | 45385.4083 | 2024-04-03 15:03 | 45385.6271 | 0.018571 | 5.8955e-05 | 2 | 630 | Planned | Planned interruption | DDE connection
28 |  | SKE1416 | TX A546 CCT3 |  | Waimate | 2024-04-04 08:31 | 45386.3549 | 2024-04-04 16:33 | 45386.6896 | 0.44046 | 0.00091381 | 31 | 14942 | Planned | Planned interruption | TX Replacement
29 |  | SKE1416 | TX A546 CCT2 |  | Waimate | 2024-04-04 08:31 | 45386.3549 | 2024-04-04 16:22 | 45386.6819 | 0.20826 | 0.00044216 | 15 | 7065 | Planned | Planned interruption | TX Replacement
30 |  | SKE1416 | Pole 20795 Links W749-TX A546 CCT3-TX A546 CCT2-TX A790 CCT2 |  | Waimate | 2024-04-04 08:31 | 45386.3549 | 2024-04-04 16:05 | 45386.6701 | 1.887 | 0.0041563 | 141 | 64014 | Planned | Planned interruption | TX Replacement
31 |  | RAK137 | TX E311 CCT2 |  | Lakeside Drive | 2024-04-04 13:09 | 45386.5479 | 2024-04-04 15:17 | 45386.6368 | 0.0075463 | 5.8955e-05 | 2 | 256 | Planned | Planned interruption | TX Replacement
32 |  | RAK137 | TX E311 CCT3 |  | Lakeside Drive | 2024-04-04 13:09 | 45386.5479 | 2024-04-04 15:22 | 45386.6403 | 0.0039205 | 2.9478e-05 | 1 | 133 | Planned | Planned interruption | TX Replacement
33 |  | 3866 | CB G297 to ABS G173 & ABS G170 |  | Winchester | 2024-04-06 00:32 | 45388.0222 | 2024-04-06 13:00 | 45388.5417 | 1.0363 | 0.0013854 | 47 | 35156 | Unplanned | Adverse environment | Fire In hedge Line
34 |  | 3866 | ABS G173 to end |  | Winchester | 2024-04-06 00:32 | 45388.0222 | 2024-04-06 03:08 | 45388.1306 | 0.087372 | 0.00056008 | 19 | 2964 | Unplanned | Adverse environment | Fire In hedge Line
35 |  | 3866 | ABS G170 to end minus ABS G160 |  | Winchester | 2024-04-06 00:32 | 45388.0222 | 2024-04-06 03:08 | 45388.1306 | 0.77715 | 0.0049817 | 169 | 26364 | Unplanned | Adverse environment | Fire In hedge Line
36 |  | 3866 | ABS G160 to end |  | Winchester | 2024-04-06 00:32 | 45388.0222 | 2024-04-06 01:35 | 45388.066 | 0.18942 | 0.0030067 | 102 | 6426 | Unplanned | Adverse environment | Fire In hedge Line
37 |  | 5031 | Fuses L707 to end |  | Hadlow | 2024-04-09 06:28 | 45391.2694 | 2024-04-09 08:09 | 45391.3396 | 0.068477 | 0.00067799 | 23 | 2323 | Unplanned | Unknown | 2x Blown drop outs
38 |  | GWM1129 | ABS F277 |  | Fairlie Rural | 2024-04-09 09:00 | 45391.375 | 2024-04-09 12:43 | 45391.5299 | 0.18406 | 0.00082537 | 28 | 6244 | Planned | Planned interruption | Tree cutting
39 |  | 4307 | M338 less M452 (pole #55422) |  | Simons | 2024-04-09 19:23 | 45391.8076 | 2024-04-09 20:20 | 45391.8472 | 0.031924 | 0.00056008 | 19 | 1083 | Unplanned | Defective equipment | Burnt jumper pole #51666
40 |  | 4307 | M452 (pole #55422) end |  | Simons | 2024-04-09 19:23 | 45391.8076 | 2024-04-09 21:40 | 45391.9028 | 0.084807 | 0.00061903 | 21 | 2877 | Unplanned | Defective equipment | Burnt jumper pole #51666
41 |  | ACD115 | Switch W556 to end minus ICP #0006650232AL652 minus ICP #0006650155AL76B |  | Tawai | 2024-04-10 08:00 | 45392.3333 | 2024-04-10 17:03 | 45392.7104 | 0.48019 | 0.00088433 | 30 | 16290 | Planned | Planned interruption | Pole replacements
42 |  | ACD115 | ICP #0006650232AL652 |  | Tawai | 2024-04-10 08:00 | 45392.3333 | 2024-04-10 17:16 | 45392.7194 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | Pole replacements
43 |  | ACD115 | ICP #0006650155AL76B |  | Tawai | 2024-04-10 08:00 | 45392.3333 | 2024-04-10 17:10 | 45392.7153 | 0.016213 | 2.9478e-05 | 1 | 550 | Planned | Planned interruption | Pole replacements
44 |  | 5061 | Tripsavers W308 |  | Otaio | 2024-04-10 13:27 | 45392.5604 | 2024-04-10 16:16 | 45392.6778 | 0.059781 | 0.00035373 | 12 | 2028 | Unplanned | Defective equipment | Broken Jumper
45 |  | ACD116 | ABS W555-A1365-A311-A1559-A1300 |  | Tawai | 2024-04-11 08:00 | 45393.3333 | 2024-04-11 16:19 | 45393.6799 | 0.13238 | 0.0002653 | 9 | 4491 | Planned | Planned interruption | Pole replacements
46 |  | ACD116 | TX A1365 |  | Tawai | 2024-04-11 08:00 | 45393.3333 | 2024-04-11 16:52 | 45393.7028 | 0.062728 | 0.00011791 | 4 | 2128 | Planned | Planned interruption | Pole replacements
47 |  | ACD116 | TX A311 |  | Tawai | 2024-04-11 08:00 | 45393.3333 | 2024-04-11 16:44 | 45393.6972 | 0.061785 | 0.00011791 | 4 | 2096 | Planned | Planned interruption | Pole replacements
48 |  | ACD116 | TX A1559 |  | Tawai | 2024-04-11 08:00 | 45393.3333 | 2024-04-11 16:38 | 45393.6931 | 0.015269 | 2.9478e-05 | 1 | 518 | Planned | Planned interruption | Pole replacements
49 |  | ACD116 | TX A1300 |  | Tawai | 2024-04-11 08:00 | 45393.3333 | 2024-04-11 16:30 | 45393.6875 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Pole replacements
50 |  | JJV138 | Fuses B1916 to end |  | Hadlow | 2024-04-11 10:05 | 45393.4201 | 2024-04-11 13:20 | 45393.5556 | 0.017244 | 8.8433e-05 | 3 | 585 | Planned | Planned interruption | Liven DB4828
51 |  | 164 | STU CB1 (Otaio) to end |  | Otaio | 2024-04-12 01:34 | 45394.0653 | 2024-04-12 02:23 | 45394.0993 | 0.50554 | 0.010317 | 350 | 17150 | Unplanned | Vegetation | Bark on line pole 31701
52 |  | 164 | STU CB8 (Mt Studholme) to end |  | Mt Studholme | 2024-04-12 01:34 | 45394.0653 | 2024-04-12 02:25 | 45394.1007 | 0.51565 | 0.010111 | 343 | 17493 | Unplanned | Vegetation | Bark on line pole 31701
53 |  | 3011 | STU CB1 (Otaio) to end |  | Otaio | 2024-04-12 03:03 | 45394.1271 | 2024-04-12 06:34 | 45394.2736 | 2.1769 | 0.010317 | 350 | 73850 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark
54 |  | 3011 | STU CB8 (Mt Studholme) to end |  | Mt Studholme | 2024-04-12 04:49 | 45394.2007 | 2024-04-12 06:35 | 45394.2743 | 1.0717 | 0.010111 | 343 | 36358 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark
55 |  | 3011 | W100 to end |  | Morven | 2024-04-12 04:50 | 45394.2014 | 2024-04-12 06:18 | 45394.2625 | 0.028534 | 0.00032425 | 11 | 968 | Unplanned | Defective equipment | Burnt jumper pole 31678 due to fault current from the bark
56 |  | ACD117 | TX A311 |  | Tawai | 2024-04-12 08:00 | 45394.3333 | 2024-04-12 15:53 | 45394.6618 | 0.055772 | 0.00011791 | 4 | 1892 | Planned | Planned interruption | Pole replacements
57 |  | ACD117 | ABS W555-TX A311 |  | Tawai | 2024-04-12 08:00 | 45394.3333 | 2024-04-12 15:16 | 45394.6361 | 0.19278 | 0.00044216 | 15 | 6540 | Planned | Planned interruption | Pole replacements
58 |  | SLA547 | Fuses A387 to end |  | Waikakahi | 2024-04-12 09:15 | 45394.3854 | 2024-04-12 10:03 | 45394.4187 | 0.0042448 | 8.8433e-05 | 3 | 144 | Unplanned | Third party interference | Tx maintenance
59 |  | 3012 | CB T127 to end less T404, TX62, T667 & TX66 |  | Rangitata | 2024-04-13 03:18 | 45395.1375 | 2024-04-13 05:57 | 45395.2479 | 0.14998 | 0.00094328 | 32 | 5088 | Unplanned | Wildlife | Possum at pole #06748
60 |  | 3012 | T404 to end |  | Rangitata | 2024-04-13 03:18 | 45395.1375 | 2024-04-13 06:06 | 45395.2542 | 0.064379 | 0.00038321 | 13 | 2184 | Unplanned | Wildlife | Possum at pole #06748
61 |  | 3012 | T667 to end |  | Rangitata | 2024-04-13 03:18 | 45395.1375 | 2024-04-13 06:13 | 45395.259 | 0.041269 | 0.00023582 | 8 | 1400 | Unplanned | Wildlife | Possum at pole #06748
62 |  | 3012 | TX62 to end |  | Rangitata | 2024-04-13 03:18 | 45395.1375 | 2024-04-13 06:17 | 45395.2618 | 0.047489 | 0.0002653 | 9 | 1611 | Unplanned | Wildlife | Possum at pole #06748
63 |  | 3012 | TX66 to end |  | Rangitata | 2024-04-13 03:18 | 45395.1375 | 2024-04-13 06:11 | 45395.2576 | 0.061196 | 0.00035373 | 12 | 2076 | Unplanned | Wildlife | Possum at pole #06748
64 |  | SKE1727 | TX B1245 CCT4 |  | Levels Plain | 2024-04-14 08:00 | 45396.3333 | 2024-04-14 14:46 | 45396.6153 | 0.15558 | 0.00038321 | 13 | 5278 | Planned | Planned interruption | Removal of redundant 33kV lines
65 |  | SKE1727 | RMU L1264-CB L876-RMU L1140-TX B1245 CCT4 |  | Levels Plain | 2024-04-14 08:00 | 45396.3333 | 2024-04-14 14:44 | 45396.6139 | 0.29772 | 0.00073694 | 25 | 10100 | Planned | Planned interruption | Removal of redundant 33kV lines
66 |  | GWM1141 | Fuses T119 |  | Milford | 2024-04-15 09:01 | 45397.3757 | 2024-04-15 12:20 | 45397.5139 | 0.19945 | 0.0010022 | 34 | 6766 | Planned | Planned interruption | Tree cutting
67 |  | 4401 | M346 - M318 |  | TEK-UHT 33kV | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 20:30 | 45397.8542 | 0.033899 | 0.00029478 | 10 | 1150 | Unplanned | Unknown | Unknown - possible bird strike
68 |  | 4401 | M73 - M272 - M24 |  | TEK-UHT 33kV | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:04 | 45397.9194 | 0.07393 | 0.00035373 | 12 | 2508 | Unplanned | Unknown | Unknown - possible bird strike
69 |  | 4401 | M272 |  | TEK-UHT 33kV | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:06 | 45397.9208 | 0.031099 | 0.00014739 | 5 | 1055 | Unplanned | Unknown | Unknown - possible bird strike
70 |  | 4401 | M158 |  | M158 | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:06 | 45397.9208 | 0.099517 | 0.00047164 | 16 | 3376 | Unplanned | Unknown | Unknown - possible bird strike
71 |  | 4401 | M159 |  | M159 | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:06 | 45397.9208 | 0.43538 | 0.0020634 | 70 | 14770 | Unplanned | Unknown | Unknown - possible bird strike
72 |  | 4401 | M24 |  | TEK-UHT 33kV | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:08 | 45397.9222 | 0.087902 | 0.00041269 | 14 | 2982 | Unplanned | Unknown | Unknown - possible bird strike
73 |  | RAK136 | TE12-TE12 CCT11-TE12 CCT18 |  | Hayes Street | 2024-04-15 22:00 | 45397.9167 | 2024-04-15 22:32 | 45397.9389 | 0.016979 | 0.0005306 | 18 | 576 | Planned | Planned interruption | Pre work for planned outage for Lucy box replacement
74 |  | SLA542A | Fuses TO C356 |  | Fairlie Rural | 2024-04-16 09:00 | 45398.375 | 2024-04-16 11:46 | 45398.4903 | 0.048933 | 0.00029478 | 10 | 1660 | Planned | Planned interruption | Tree cutting
75 |  | ACD125 | TX B1073-3ph ICP from p#28301-other ICPs fed from P#28301 |  | Hadlow | 2024-04-16 09:00 | 45398.375 | 2024-04-16 14:23 | 45398.5993 | 0.0095213 | 2.9478e-05 | 1 | 323 | Planned | Planned interruption | Red Tag pole replacement
76 |  | ACD125 | 3ph ICP fed from p#28301 |  | Hadlow | 2024-04-16 09:00 | 45398.375 | 2024-04-16 14:32 | 45398.6056 | 0.0097866 | 2.9478e-05 | 1 | 332 | Planned | Planned interruption | Red Tag pole replacement
77 |  | ACD125 | ICPs fed from P#28301-3ph ICP fed from pole #28301 |  | Hadlow | 2024-04-16 09:00 | 45398.375 | 2024-04-16 14:50 | 45398.6181 | 0.020634 | 5.8955e-05 | 2 | 700 | Planned | Planned interruption | Red Tag pole replacement
78 |  | 5062 | RGA CB4-ABS T415 |  | Old Main South Road | 2024-04-16 15:55 | 45398.6632 | 2024-04-16 16:33 | 45398.6896 | 0.082891 | 0.0021813 | 74 | 2812 | Unplanned | Defective equipment | Fault - Broken conductor
79 |  | 5062 | ABS T415 |  | Old Main South Road | 2024-04-16 15:55 | 45398.6632 | 2024-04-16 19:12 | 45398.8 | 0.11614 | 0.00058955 | 20 | 3940 | Unplanned | Defective equipment | Fault Broken conductor
80 |  | HTR001 | ABS G204-ABS TX38 |  | Speechley | 2024-04-17 08:00 | 45399.3333 | 2024-04-17 13:11 | 45399.5493 | 0.38504 | 0.0012381 | 42 | 13062 | Planned | Planned interruption | Tree cutting
81 |  | ACD118 | TX A1038 |  | Morven | 2024-04-17 08:05 | 45399.3368 | 2024-04-17 17:11 | 45399.716 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Line Maintenance
82 |  | ACD118 | TX A297 |  | Morven | 2024-04-17 08:05 | 45399.3368 | 2024-04-17 17:22 | 45399.7236 | 0.032838 | 5.8955e-05 | 2 | 1114 | Planned | Planned interruption | Line Maintenance
83 |  | ACD118 | TX A531 |  | Morven | 2024-04-17 08:05 | 45399.3368 | 2024-04-17 17:12 | 45399.7167 | 0.016124 | 2.9478e-05 | 1 | 547 | Planned | Planned interruption | Line Maintenance
84 |  | ACD118 | ABS W112-Temp links pole 54387-TX A1038-TX A297-TX A531 |  | Morven | 2024-04-17 08:05 | 45399.3368 | 2024-04-17 16:49 | 45399.7007 | 0.13902 | 0.0002653 | 9 | 4716 | Planned | Planned interruption | Line Maintenance
85 |  | HTR003 | Fuses T217 |  | Waitohi | 2024-04-18 08:00 | 45400.3333 | 2024-04-18 09:54 | 45400.4125 | 0.07057 | 0.00061903 | 21 | 2394 | Planned | Planned interruption | Tree cutting
86 |  | ACD123 | TX A94 |  | Otaio | 2024-04-18 08:30 | 45400.3542 | 2024-04-18 16:55 | 45400.7049 | 0.029772 | 5.8955e-05 | 2 | 1010 | Planned | Planned interruption | Red Tag Pole replacement
87 |  | ACD123 | Fuses W316-TX A94 |  | Otaio | 2024-04-18 08:30 | 45400.3542 | 2024-04-18 16:37 | 45400.6924 | 0.15791 | 0.00032425 | 11 | 5357 | Planned | Planned interruption | Red Tag Pole replacement
88 |  | SKE1684 | TX B992 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:54 | 45400.6625 | 0.085426 | 0.00020634 | 7 | 2898 | Planned | Planned interruption | TX Maintenance
89 |  | SKE1684 | B960 CCT3 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:43 | 45400.6549 | 0.11879 | 0.00029478 | 10 | 4030 | Planned | Planned interruption | TX Maintenance
90 |  | SKE1684 | B960 CCT2 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:43 | 45400.6549 | 0.10692 | 0.0002653 | 9 | 3627 | Planned | Planned interruption | TX Maintenance
91 |  | SKE1684 | B1021 CCT5 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:43 | 45400.6549 | 0.15443 | 0.00038321 | 13 | 5239 | Planned | Planned interruption | TX Maintenance
92 |  | SKE1684 | B1021 CCT4 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:43 | 45400.6549 | 0.16631 | 0.00041269 | 14 | 5642 | Planned | Planned interruption | TX Maintenance
93 |  | SKE1684 | B1021 CCT3 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:42 | 45400.6542 | 0.2133 | 0.0005306 | 18 | 7236 | Planned | Planned interruption | TX Maintenance
94 |  | SKE1684 | B1097 CCT5 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:50 | 45400.6597 | 0.24172 | 0.00058955 | 20 | 8200 | Planned | Planned interruption | TX Maintenance
95 |  | SKE1684 | B1097 CCT3 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:50 | 45400.6597 | 0.1692 | 0.00041269 | 14 | 5740 | Planned | Planned interruption | TX Maintenance
96 |  | SKE1684 | B1097 CCT4 |  | Morgans Rd | 2024-04-18 09:00 | 45400.375 | 2024-04-18 15:50 | 45400.6597 | 0.15712 | 0.00038321 | 13 | 5330 | Planned | Planned interruption | TX Maintenance
97 |  | 5032 | T325 |  | Speechley | 2024-04-18 12:30 | 45400.5208 | 2024-04-18 14:20 | 45400.5972 | 0.058366 | 0.0005306 | 18 | 1980 | Unplanned | Defective equipment | Conductor Repairs at Pole #09713
98 |  | HTR004 | Fuses T309 |  | Waitohi | 2024-04-18 13:00 | 45400.5417 | 2024-04-18 14:55 | 45400.6215 | 0.071189 | 0.00061903 | 21 | 2415 | Planned | Planned interruption | Tree cutting
99 |  | 4402 | T127 |  | Rangitata | 2024-04-18 17:00 | 45400.7083 | 2024-04-18 19:09 | 45400.7979 | 0.28139 | 0.0021813 | 74 | 9546 | Unplanned | Unknown | Unknown
100 |  | 5063 | TX B1553 |  | Arowhenua | 2024-04-19 08:13 | 45401.3424 | 2024-04-19 15:42 | 45401.6542 | 0.026471 | 5.8955e-05 | 2 | 898 | Unplanned | Defective equipment | Faulty TX replacement
101 |  | ACD124 | Links W440 |  | Otaio | 2024-04-19 08:30 | 45401.3542 | 2024-04-19 14:03 | 45401.5854 | 0.098161 | 0.00029478 | 10 | 3330 | Planned | Planned interruption | Red Tag Pole replacement
102 |  | 5063 | Fuses L879-TX B1553 |  | Arowhenua | 2024-04-19 13:53 | 45401.5785 | 2024-04-19 15:34 | 45401.6486 | 0.026795 | 0.0002653 | 9 | 909 | Unplanned | Defective equipment | Faulty TX replacement
103 |  | 4403 | W527 - TO A969 |  | Waikakahi | 2024-04-21 15:40 | 45403.6528 | 2024-04-21 16:52 | 45403.7028 | 0.0084896 | 0.00011791 | 4 | 288 | Unplanned | Defective equipment | Replace Faulty Tx A969
104 |  | 4403 | TO A969 |  | Waikakahi | 2024-04-21 15:40 | 45403.6528 | 2024-04-21 17:17 | 45403.7201 | 0.0028593 | 2.9478e-05 | 1 | 97 | Unplanned | Defective equipment | Replace Faulty Tx A969
105 |  | 5038 | Fuses TO C464 |  | Fairlie Rural | 2024-04-22 15:57 | 45404.6646 | 2024-04-22 17:03 | 45404.7104 | 0.0019455 | 2.9478e-05 | 1 | 66 | Unplanned | Defective equipment | Broken Stay
106 |  | ACD119 | Pole 54387 temp links-Links W363-TX A483 |  | Morven | 2024-04-23 08:00 | 45405.3333 | 2024-04-23 16:37 | 45405.6924 | 0.74676 | 0.0014444 | 49 | 25333 | Planned | Planned interruption | Crowes Rd Maint
107 |  | ACD119 | TX A483 |  | Morven | 2024-04-23 08:00 | 45405.3333 | 2024-04-23 17:00 | 45405.7083 | 0.063672 | 0.00011791 | 4 | 2160 | Planned | Planned interruption | Crowes Rd Maint
108 |  | GWM1148 | Fuses L827 |  | Hadlow | 2024-04-23 09:00 | 45405.375 | 2024-04-23 11:53 | 45405.4951 | 0.18869 | 0.0010907 | 37 | 6401 | Planned | Planned interruption | Tree cutting
109 |  | SRT200 | Fuses G245 |  | Speechley | 2024-04-24 08:30 | 45406.3542 | 2024-04-24 14:28 | 45406.6028 | 0.1583 | 0.00044216 | 15 | 5370 | Planned | Planned interruption | New TX
110 |  | 5035 | F179 |  | Fairlie Rural | 2024-04-24 16:55 | 45406.7049 | 2024-04-24 17:35 | 45406.7326 | 0.0058955 | 0.00014739 | 5 | 200 | Unplanned | Defective equipment | Replace missing nut on P#10916
111 |  | 5037 | Fuses F220 |  | Fairlie Rural | 2024-04-25 10:39 | 45407.4437 | 2024-04-25 13:49 | 45407.5757 | 0.12322 | 0.00064851 | 22 | 4180 | Unplanned | Unknown | Unknown
112 |  | 5036 | W664 - W263 |  | Waihaorunga | 2024-04-25 11:15 | 45407.4688 | 2024-04-25 11:36 | 45407.4833 | 0.095331 | 0.0045396 | 154 | 3234 | Unplanned | Unknown | Unknown
113 |  | 5036 | W263 - W258 |  | Waihaorunga | 2024-04-25 11:15 | 45407.4688 | 2024-04-25 11:45 | 45407.4896 | 0.29537 | 0.0098455 | 334 | 10020 | Unplanned | Unknown | Unknown
114 |  | 5036 | W258 - W708 |  | Waihaorunga | 2024-04-25 11:15 | 45407.4688 | 2024-04-25 11:54 | 45407.4958 | 0.067828 | 0.0017392 | 59 | 2301 | Unplanned | Unknown | Unknown
115 |  | 5036 | W708 |  | Waihaorunga | 2024-04-25 11:15 | 45407.4688 | 2024-04-25 12:05 | 45407.5035 | 0.37142 | 0.0074284 | 252 | 12600 | Unplanned | Unknown | Unknown
116 |  | 5034 | T598 |  | Speechley | 2024-04-25 13:12 | 45407.55 | 2024-04-25 16:21 | 45407.6813 | 0.011143 | 5.8955e-05 | 2 | 378 | Unplanned | Adverse weather | Strong Wind - Part of roof on line
117 |  | 5033 | W674 |  | Otaio | 2024-04-25 15:00 | 45407.625 | 2024-04-25 16:04 | 45407.6694 | 0.018866 | 0.00029478 | 10 | 640 | Unplanned | Adverse weather | Strong Wind - Tree branch on line
118 |  | 4404 | W291 - W653 |  | Morven | 2024-04-26 14:43 | 45408.6132 | 2024-04-26 16:06 | 45408.6708 | 0.10031 | 0.0012086 | 41 | 3403 | Unplanned | Defective equipment | Broken Jumper @ Links W742
119 |  | SKE1731 | DB H107 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:44 | 45412.7806 | 0.35762 | 0.0005306 | 18 | 12132 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
120 |  | SKE1731 | DB H95 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 19:07 | 45412.7965 | 0.12328 | 0.00017687 | 6 | 4182 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
121 |  | SKE1731 | DB H94 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:55 | 45412.7882 | 0.080769 | 0.00011791 | 4 | 2740 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
122 |  | SKE1731 | TE87 CCT17 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:33 | 45412.7729 | 0.42996 | 0.00064851 | 22 | 14586 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
123 |  | SKE1731 | TE87-TE87 CCT17-DB H94-DB H95-DB H107 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:05 | 45412.7535 | 0.7113 | 0.0011202 | 38 | 24130 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
124 |  | SKE1731 | 24 BRUNSWICK ST |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:08 | 45412.7556 | 0.018807 | 2.9478e-05 | 1 | 638 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
125 |  | SKE1731 | 24 GIBSON ST |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:07 | 45412.7549 | 0.018777 | 2.9478e-05 | 1 | 637 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
126 |  | SKE1731 | 82 CHURCH ST |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 18:04 | 45412.7528 | 0.018689 | 2.9478e-05 | 1 | 634 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
127 |  | SKE1731 | HNT CB7-82 CHURCH-24 GIBSON-24 BRUNSWICK-TE87-TE20 |  | Church Street South Side | 2024-04-30 07:30 | 45412.3125 | 2024-04-30 17:56 | 45412.7472 | 2.3066 | 0.0036847 | 125 | 78250 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
128 |  | SRT201 | Temp links pole 26443 |  | Sutherland | 2024-04-30 09:00 | 45412.375 | 2024-04-30 15:08 | 45412.6306 | 0.065087 | 0.00017687 | 6 | 2208 | Planned | Planned interruption | Line Maintenance
129 |  | 5064 | TX D1067 |  | Woodbury | 2024-04-30 09:11 | 45412.3826 | 2024-04-30 09:18 | 45412.3875 | 0.0022698 | 0.00032425 | 11 | 77 | Unplanned | Vegetation | Branch on LV line removal
130 |  | ACD121 | TX A296 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:40 | 45413.7361 | 0.017097 | 2.9478e-05 | 1 | 580 | Planned | Planned interruption | Crowes Rd Maint
131 |  | ACD121 | Fuses W656 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:41 | 45413.7368 | 0.23977 | 0.00041269 | 14 | 8134 | Planned | Planned interruption | Crowes Rd Maint
132 |  | ACD121 | Fuses W655 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:37 | 45413.734 | 0.23812 | 0.00041269 | 14 | 8078 | Planned | Planned interruption | Crowes Rd Maint
133 |  | ACD121 | ABS W496 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:35 | 45413.7326 | 0.033899 | 5.8955e-05 | 2 | 1150 | Planned | Planned interruption | Crowes Rd Maint
134 |  | ACD121 | TX A552 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:32 | 45413.7306 | 0.016861 | 2.9478e-05 | 1 | 572 | Planned | Planned interruption | Crowes Rd Maint
135 |  | ACD121 | TX A529 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:45 | 45413.7396 | 0.18969 | 0.00032425 | 11 | 6435 | Planned | Planned interruption | Crowes Rd Maint
136 |  | ACD121 | TX A283 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:41 | 45413.7368 | 0.068506 | 0.00011791 | 4 | 2324 | Planned | Planned interruption | Crowes Rd Maint
137 |  | ACD121 | Fuses W164 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:36 | 45413.7333 | 0.3226 | 0.00056008 | 19 | 10944 | Planned | Planned interruption | Crowes Rd Maint
138 |  | ACD121 | ABS W299 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:30 | 45413.7292 | 0.033605 | 5.8955e-05 | 2 | 1140 | Planned | Planned interruption | Crowes Rd Maint
139 |  | ACD121 | TX A803 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:25 | 45413.7257 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Crowes Rd Maint
140 |  | ACD121 | Links W279-Temp Links Pole 38954-TX A803-ABS W299-Fuses W164-TX A283-TX A529-TX A552-ABS W496-Fuses W655-Fuses W656-TX A296 |  | Morven | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:21 | 45413.7229 | 0.049611 | 8.8433e-05 | 3 | 1683 | Planned | Planned interruption | Crowes Rd Maint
141 |  | SKE1732 | DB H93 |  | Church Street South Side | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:20 | 45413.7222 | 0.14857 | 0.0002653 | 9 | 5040 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
142 |  | SKE1732 | DB H92 |  | Church Street South Side | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:08 | 45413.7139 | 0.14538 | 0.0002653 | 9 | 4932 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
143 |  | SKE1732 | DB H108 service |  | Church Street South Side | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 17:13 | 45413.7174 | 0.016301 | 2.9478e-05 | 1 | 553 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
144 |  | SKE1732 | TE87 CCT15 |  | Church Street South Side | 2024-05-01 08:00 | 45413.3333 | 2024-05-01 16:57 | 45413.7063 | 0.17412 | 0.00032425 | 11 | 5907 | Planned | Planned interruption | Sub Maint & Sub replacement Grey Rd
145 |  | 5065 | ABS T493 |  | Rolleston Road | 2024-05-01 09:44 | 45413.4056 | 2024-05-01 12:53 | 45413.5368 | 0.87469 | 0.004628 | 157 | 29673 | Unplanned | Defective equipment | ABS Replacement
146 |  | 5066 | TMK CB2-ABS T116-ABS T125 |  | Milford | 2024-05-01 15:11 | 45413.6326 | 2024-05-01 17:36 | 45413.7333 | 0.29065 | 0.0020045 | 68 | 9860 | Unplanned | Defective equipment | ABS Replacement
147 |  | ACD120 | TX A892 |  | Morven | 2024-05-02 08:00 | 45414.3333 | 2024-05-02 16:25 | 45414.684 | 0.029772 | 5.8955e-05 | 2 | 1010 | Planned | Planned interruption | Crowes Rd Maint
148 |  | ACD120 | ABS W112-Temp links pole 54387-TX A892 |  | Morven | 2024-05-02 08:00 | 45414.3333 | 2024-05-02 16:20 | 45414.6806 | 0.16213 | 0.00032425 | 11 | 5500 | Planned | Planned interruption | Crowes Rd Maint
149 |  | JDJ080 | TX B260-233 Kerrytown Rd-240 Kerrytown Rd |  | Waitawa | 2024-05-02 08:33 | 45414.3562 | 2024-05-02 10:26 | 45414.4347 | 0.003331 | 2.9478e-05 | 1 | 113 | Planned | Planned interruption | Change TX from 1ph to 2ph
150 |  | JDJ080 | 233 Kerrytown Rd |  | Waitawa | 2024-05-02 08:33 | 45414.3562 | 2024-05-02 10:28 | 45414.4361 | 0.0033899 | 2.9478e-05 | 1 | 115 | Planned | Planned interruption | Change TX from 1ph to 2ph
151 |  | JDJ080 | 240 Kerrytown Rd |  | Waitawa | 2024-05-02 08:33 | 45414.3562 | 2024-05-02 11:10 | 45414.4653 | 0.004628 | 2.9478e-05 | 1 | 157 | Planned | Planned interruption | Change TX from 1ph to 2ph
152 |  | ACD122/GWM1144 | TX A1038 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:46 | 45415.7403 | 0.017274 | 2.9478e-05 | 1 | 586 | Planned | Planned interruption | Crowes Rd Maint
153 |  | ACD122/GWM1144 | TX A1539 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:40 | 45415.7361 | 0.017097 | 2.9478e-05 | 1 | 580 | Planned | Planned interruption | Crowes Rd Maint
154 |  | ACD122/GWM1144 | TX A835 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:36 | 45415.7333 | 0.033958 | 5.8955e-05 | 2 | 1152 | Planned | Planned interruption | Crowes Rd Maint
155 |  | ACD122/GWM1144 | Fuses W656 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:47 | 45415.741 | 0.24225 | 0.00041269 | 14 | 8218 | Planned | Planned interruption | Crowes Rd Maint
156 |  | ACD122/GWM1144 | Fuses W655 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:44 | 45415.7389 | 0.24101 | 0.00041269 | 14 | 8176 | Planned | Planned interruption | Crowes Rd Maint
157 |  | ACD122/GWM1144 | ABS W496 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:42 | 45415.7375 | 0.034312 | 5.8955e-05 | 2 | 1164 | Planned | Planned interruption | Crowes Rd Maint
158 |  | ACD122/GWM1144 | TX A552 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:36 | 45415.7333 | 0.033958 | 5.8955e-05 | 2 | 1152 | Planned | Planned interruption | Crowes Rd Maint
159 |  | ACD122/GWM1144 | TX A529 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:47 | 45415.741 | 0.19034 | 0.00032425 | 11 | 6457 | Planned | Planned interruption | Crowes Rd Maint
160 |  | ACD122/GWM1144 | TX A283 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:45 | 45415.7396 | 0.068978 | 0.00011791 | 4 | 2340 | Planned | Planned interruption | Crowes Rd Maint
161 |  | ACD122/GWM1144 | Fuses W164 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:43 | 45415.7382 | 0.32652 | 0.00056008 | 19 | 11077 | Planned | Planned interruption | Crowes Rd Maint
162 |  | ACD122/GWM1144 | ABS W299 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:40 | 45415.7361 | 0.034194 | 5.8955e-05 | 2 | 1160 | Planned | Planned interruption | Crowes Rd Maint
163 |  | ACD122/GWM1144 | TX A803 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:35 | 45415.7326 | 0.01695 | 2.9478e-05 | 1 | 575 | Planned | Planned interruption | Crowes Rd Maint
164 |  | ACD122/GWM1144 | ABS W190-CB W245-TX A803-ABS W299-Fuses W164-TX A283-TX A529-TX A552-ABS W496-Fuses W655-Fuses W656-TX A835-TX A1539-TX A1038 |  | Morven | 2024-05-03 08:00 | 45415.3333 | 2024-05-03 17:32 | 45415.7306 | 1.1971 | 0.0020929 | 71 | 40612 | Planned | Planned interruption | Crowes Rd Maint
165 |  | SRT202/GWM1152 | ABS W264 |  | Morven | 2024-05-03 09:00 | 45415.375 | 2024-05-03 13:58 | 45415.5819 | 0.24596 | 0.00082537 | 28 | 8344 | Planned | Planned interruption | Red tag pole replacement & Tree cutting
166 |  | 5119 | CB T127 to end minus T404, TX62, T667 & TX62 |  | Rangitata | 2024-05-05 20:53 | 45417.8701 | 2024-05-05 22:18 | 45417.9292 | 0.080179 | 0.00094328 | 32 | 2720 | Unplanned | Unknown | Unknown
167 |  | 5119 | TX62 to end |  | Rangitata | 2024-05-05 20:53 | 45417.8701 | 2024-05-05 22:34 | 45417.9403 | 0.026795 | 0.0002653 | 9 | 909 | Unplanned | Unknown | Unknown
168 |  | 5119 | TX66 to end |  | Rangitata | 2024-05-05 20:53 | 45417.8701 | 2024-05-05 22:39 | 45417.9437 | 0.037496 | 0.00035373 | 12 | 1272 | Unplanned | Unknown | Unknown
169 |  | 5119 | T667 to end |  | Rangitata | 2024-05-05 20:53 | 45417.8701 | 2024-05-05 22:52 | 45417.9528 | 0.028063 | 0.00023582 | 8 | 952 | Unplanned | Unknown | Unknown
170 |  | 5119 | T404 to end |  | Rangitata | 2024-05-05 20:53 | 45417.8701 | 2024-05-05 23:23 | 45417.9743 | 0.057481 | 0.00038321 | 13 | 1950 | Unplanned | Unknown | Unknown
171 |  | ACD126 | TX D217 |  | Rolleston Road | 2024-05-06 09:40 | 45418.4028 | 2024-05-06 14:30 | 45418.6042 | 0.017097 | 5.8955e-05 | 2 | 580 | Planned | Planned interruption | Pole Replacement
172 |  | JDJ073 | TX D899 CCT3 |  | Temuka East | 2024-05-06 10:44 | 45418.4472 | 2024-05-06 16:29 | 45418.6868 | 0.37628 | 0.0010907 | 37 | 12765 | Planned | Planned interruption | LV Fuse work
173 |  | JDJ073 | TX D899 CCT2 |  | Temuka East | 2024-05-06 10:44 | 45418.4472 | 2024-05-06 15:57 | 45418.6646 | 0.1384 | 0.00044216 | 15 | 4695 | Planned | Planned interruption | LV fuse work
174 |  | JDJ081 | TX D142 |  | Waitohi | 2024-05-07 08:30 | 45419.3542 | 2024-05-07 16:53 | 45419.7035 | 0.014827 | 2.9478e-05 | 1 | 503 | Planned | Planned interruption | Red Tagged Pole replacement
175 |  | JDJ081 | Fuses T305-TX D142 |  | Waitohi | 2024-05-07 08:30 | 45419.3542 | 2024-05-07 16:38 | 45419.6931 | 0.14385 | 0.00029478 | 10 | 4880 | Planned | Planned interruption | Red Tagged Pole replacement
176 |  | SKE1626 | TX D1393 |  | Old Main South Road | 2024-05-07 09:18 | 45419.3875 | 2024-05-07 17:10 | 45419.7153 | 0.04174 | 8.8433e-05 | 3 | 1416 | Planned | Planned interruption | TX Maintenance
177 |  | 4405 | TO A1419 |  | St Andrews | 2024-05-07 11:13 | 45419.4674 | 2024-05-07 15:58 | 45419.6653 | 0.0084011 | 2.9478e-05 | 1 | 285 | Unplanned | Third party interference | Lines down - caused by logger truck
178 |  | ACD127 | TX A65 |  | St Andrews | 2024-05-08 09:00 | 45420.375 | 2024-05-08 16:55 | 45420.7049 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Pole Replacement
179 |  | ACD127 | Fuses W460-TX A65 |  | St Andrews | 2024-05-08 09:00 | 45420.375 | 2024-05-08 16:35 | 45420.691 | 0.040237 | 8.8433e-05 | 3 | 1365 | Planned | Planned interruption | Pole Replacement
180 |  | SKE1671 | TX B1348 |  | Mountainview | 2024-05-08 09:02 | 45420.3764 | 2024-05-08 14:10 | 45420.5903 | 0.29053 | 0.00094328 | 32 | 9856 | Planned | Planned interruption | TX Maintenance
181 |  | 5039 | TO A48 |  | St Andrews | 2024-05-08 14:57 | 45420.6229 | 2024-05-08 15:02 | 45420.6264 | 0.00029478 | 5.8955e-05 | 2 | 10 | Unplanned | Defective equipment | Remove broken Stay @ P#29044
182 |  | 988 | CB F295 |  | Cave | 2024-05-08 15:46 | 45420.6569 | 2024-05-08 16:58 | 45420.7069 | 0.070039 | 0.00097276 | 33 | 2376 | Unplanned | Adverse weather | Strong winds
183 |  | 989 | Fuses G174 |  | Winchester | 2024-05-08 16:17 | 45420.6785 | 2024-05-08 17:40 | 45420.7361 | 0.046486 | 0.00056008 | 19 | 1577 | Unplanned | Vegetation | Branch on line
184 |  | SKE1687 | TX D1274 |  | Milford | 2024-05-09 09:32 | 45421.3972 | 2024-05-09 15:06 | 45421.6292 | 0.039382 | 0.00011791 | 4 | 1336 | Planned | Planned interruption | Defect repairs
185 |  | RAK138 | ABS T234 |  | Temuka West | 2024-05-11 08:04 | 45423.3361 | 2024-05-11 17:08 | 45423.7139 | 0.016036 | 2.9478e-05 | 1 | 544 | Planned | Planned interruption | NZI Maintenance
186 |  | 5018 | ABS M26 |  | Haldon-Lilybank 22kV | 2024-05-11 12:10 | 45423.5069 | 2024-05-11 13:54 | 45423.5792 | 0.076642 | 0.00073694 | 25 | 2600 | Unplanned | Third party interference | Broken Pole #23795
187 |  | ACD128 | ABS F273 |  | Fairlie Rural | 2024-05-13 08:00 | 45425.3333 | 2024-05-13 08:03 | 45425.3354 | 0.0014149 | 0.00047164 | 16 | 48 | Planned | Planned interruption | Maintenance
188 |  | ACD128 | ABS F255-ABS F277-ABS F273-TX C100 |  | Fairlie Rural | 2024-05-13 08:30 | 45425.3542 | 2024-05-13 14:22 | 45425.5986 | 0.22827 | 0.00064851 | 22 | 7744 | Planned | Planned interruption | Maintenance
189 |  | ACD128 | TX C100 |  | Fairlie Rural | 2024-05-13 08:30 | 45425.3542 | 2024-05-13 14:33 | 45425.6062 | 0.032101 | 8.8433e-05 | 3 | 1089 | Planned | Planned interruption | Maintenance
190 |  | ACD128 | ABS F273 |  | Fairlie Rural | 2024-05-13 17:15 | 45425.7188 | 2024-05-13 17:17 | 45425.7201 | 0.00094328 | 0.00047164 | 16 | 32 | Planned | Planned interruption | Maintenance
191 |  | 4406 | CB11 - T586 |  | Belfield | 2024-05-14 15:17 | 45426.6368 | 2024-05-14 16:25 | 45426.684 | 0.13831 | 0.002034 | 69 | 4692 | Unplanned | Third party interference | Car v Pole #10556
192 |  | 4406 | T585 |  | Belfield | 2024-05-14 15:17 | 45426.6368 | 2024-05-14 16:33 | 45426.6896 | 0.087372 | 0.0011496 | 39 | 2964 | Unplanned | Third party interference | Car v Pole #10556
193 |  | 4406 | T584 |  | Belfield | 2024-05-14 15:17 | 45426.6368 | 2024-05-14 16:45 | 45426.6979 | 0.046693 | 0.0005306 | 18 | 1584 | Unplanned | Third party interference | Car v Pole #10556
194 |  | 4406 | T586 - T585 - T584 |  | Belfield | 2024-05-14 15:17 | 45426.6368 | 2024-05-14 18:39 | 45426.7771 | 0.047636 | 0.00023582 | 8 | 1616 | Unplanned | Third party interference | Car v Pole #10556
195 |  | 4406 | T584 |  | Belfield | 2024-05-14 19:10 | 45426.7986 | 2024-05-14 19:12 | 45426.8 | 0.0010612 | 0.0005306 | 18 | 36 | Unplanned | Third party interference | Car v Pole #10556
196 |  | 4407 | W685 |  | Otaio | 2024-05-15 07:35 | 45427.316 | 2024-05-15 07:36 | 45427.3167 | 0.0018571 | 0.0018571 | 63 | 63 | Unplanned | Unknown | Load transfer from STU to PAR
197 |  | 4407 | W315 - W685 |  | Otaio | 2024-05-15 07:43 | 45427.3215 | 2024-05-15 07:43 | 45427.3215 | 0 | 0.0010317 | 35 | 0 | Unplanned | Unknown | Load transfer from STU to PAR
198 |  | SKE1664A | TX B1046 CCT6 |  | Mountainview | 2024-05-15 09:00 | 45427.375 | 2024-05-15 15:27 | 45427.6438 | 0.13689 | 0.00035373 | 12 | 4644 | Planned | Planned interruption | TX Maintenance
199 |  | SKE1664A | TX B1046 CCT5-LB29 |  | Mountainview | 2024-05-15 09:00 | 45427.375 | 2024-05-15 15:26 | 45427.6431 | 0.091027 | 0.00023582 | 8 | 3088 | Planned | Planned interruption | TX Maintenance
200 |  | SKE1664A | TX B1046 CCT4 |  | Mountainview | 2024-05-15 09:00 | 45427.375 | 2024-05-15 15:26 | 45427.6431 | 0.1593 | 0.00041269 | 14 | 5404 | Planned | Planned interruption | TX Maintenance
201 |  | SKE1664A | TX B1046 CCT3 |  | Mountainview | 2024-05-15 09:00 | 45427.375 | 2024-05-15 15:25 | 45427.6424 | 0.23833 | 0.00061903 | 21 | 8085 | Planned | Planned interruption | TX Maintenance
202 |  | SKE1664A | TX B1046 CCT2 |  | Mountainview | 2024-05-15 09:00 | 45427.375 | 2024-05-15 15:17 | 45427.6368 | 0.14447 | 0.00038321 | 13 | 4901 | Planned | Planned interruption | TX Maintenance
203 |  | ACD132 | TX C116 |  | Cave | 2024-05-15 09:31 | 45427.3965 | 2024-05-15 13:38 | 45427.5681 | 0.014562 | 5.8955e-05 | 2 | 494 | Planned | Planned interruption | TX Replacement
204 |  | ACD132 | Fuses F130 |  | Cave | 2024-05-15 09:31 | 45427.3965 | 2024-05-15 13:00 | 45427.5417 | 0.067769 | 0.00032425 | 11 | 2299 | Planned | Planned interruption | TX Replacement
205 |  | JDJ084 | TX A515 |  | Mt Studholme | 2024-05-16 10:00 | 45428.4167 | 2024-05-16 11:23 | 45428.4743 | 0.0024466 | 2.9478e-05 | 1 | 83 | Planned | Planned interruption | TX Replacement
206 |  | 3790 | T644 |  | Arundel | 2024-05-16 19:57 | 45428.8313 | 2024-05-16 21:41 | 45428.9035 | 0.009197 | 8.8433e-05 | 3 | 312 | Unplanned | Defective equipment | Broken jumper to Fuses T644
207 |  | 3790 | T448 - T644 |  | Arundel | 2024-05-16 21:08 | 45428.8806 | 2024-05-16 21:41 | 45428.9035 | 0.041829 | 0.0012675 | 43 | 1419 | Unplanned | Defective equipment | Broken jumper to Fuses T644
208 |  | 5019 | CB T626 |  | Rolleston Road | 2024-05-17 19:14 | 45429.8014 | 2024-05-17 20:43 | 45429.8632 | 0.4906 | 0.0055123 | 187 | 16643 | Unplanned | Unknown | Unknown
209 |  | ACD129 | TX B1994 |  | Holme Station | 2024-05-20 08:30 | 45432.3542 | 2024-05-20 15:58 | 45432.6653 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Red Tag Pole replacements
210 |  | ACD129 | ABS L123-ABS L126-TX B1994 |  | Holme Station | 2024-05-20 08:30 | 45432.3542 | 2024-05-20 15:50 | 45432.6597 | 0.33722 | 0.00076642 | 26 | 11440 | Planned | Planned interruption | Red Tag Pole replacements
211 |  | SKE1755 | TE140 CCT15-LB H24 to H253 |  | Le Cren Street | 2024-05-20 18:15 | 45432.7604 | 2024-05-20 18:21 | 45432.7646 | 0.0005306 | 8.8433e-05 | 3 | 18 | Planned | Planned interruption | TE140 Maintenenance
212 |  | SKE1755 | TE149 CCT14 |  | Le Cren Street | 2024-05-20 18:15 | 45432.7604 | 2024-05-20 18:26 | 45432.7681 | 0.0022698 | 0.00020634 | 7 | 77 | Planned | Planned interruption | TE140 Maintenenance
213 |  | SKE1755 | TE140 CCT18-DB H27 |  | Le Cren Street | 2024-05-20 18:15 | 45432.7604 | 2024-05-20 18:24 | 45432.7667 | 0.0015918 | 0.00017687 | 6 | 54 | Planned | Planned interruption | TE140 Maintenenance
214 |  | SKE1755 | TE140 CCT17 |  | Le Cren Street | 2024-05-20 18:15 | 45432.7604 | 2024-05-20 18:29 | 45432.7701 | 0.0016507 | 0.00011791 | 4 | 56 | Planned | Planned interruption | TE140 Maintenenance
215 |  | SKE1755 | TE140 CCT14 |  | Le Cren Street | 2024-05-20 18:15 | 45432.7604 | 2024-05-20 23:46 | 45432.9903 | 0.029271 | 8.8433e-05 | 3 | 993 | Planned | Planned interruption | TE140 Maintenenance
216 |  | SKE1755 | TE140 CCT18-DB H27 |  | Le Cren Street | 2024-05-20 23:33 | 45432.9812 | 2024-05-20 23:46 | 45432.9903 | 0.0022993 | 0.00017687 | 6 | 78 | Planned | Planned interruption | TE140 Maintenenance
217 |  | SKE1755 | TE140 CCT17 |  | Le Cren Street | 2024-05-20 23:34 | 45432.9819 | 2024-05-20 23:46 | 45432.9903 | 0.0014149 | 0.00011791 | 4 | 48 | Planned | Planned interruption | TE140 Maintenenance
218 |  | SKE1755 | TE140 CCT14 |  | Le Cren Street | 2024-05-20 23:38 | 45432.9847 | 2024-05-20 23:46 | 45432.9903 | 0.00070746 | 8.8433e-05 | 3 | 24 | Planned | Planned interruption | TE140 Maintenenance
219 |  | SKE1755 | TE140 CCT15-LB H24 to H253 |  | Le Cren Street | 2024-05-20 23:39 | 45432.9854 | 2024-05-20 23:46 | 45432.9903 | 0.00061903 | 8.8433e-05 | 3 | 21 | Planned | Planned interruption | TE140 Maintenenance
220 |  | SKE1735 | 69 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:57 | 45433.6646 | 0.013177 | 2.9478e-05 | 1 | 447 | Planned | Planned interruption | Pareora Line Maintenance
221 |  | SKE1735 | 70 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:48 | 45433.6583 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance
222 |  | SKE1735 | 72 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:47 | 45433.6576 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Pareora Line Maintenance
223 |  | SKE1735 | 74 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:34 | 45433.6486 | 0.012499 | 2.9478e-05 | 1 | 424 | Planned | Planned interruption | Pareora Line Maintenance
224 |  | SKE1735 | TX B45 CCT2-69,70,72,74 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:27 | 45433.6438 | 0.086045 | 0.00020634 | 7 | 2919 | Planned | Planned interruption | Pareora Line Maintenance
225 |  | SKE1735 | 12 Abbott Street |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:48 | 45433.6583 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance
226 |  | SKE1735 | TX B45 CCT4-12 Abbott Street |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:46 | 45433.6569 | 0.025705 | 5.8955e-05 | 2 | 872 | Planned | Planned interruption | Pareora Line Maintenance
227 |  | SKE1735 | 60 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:42 | 45433.6542 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Pareora Line Maintenance
228 |  | SKE1735 | 61 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:40 | 45433.6528 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Pareora Line Maintenance
229 |  | SKE1735 | 63 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:38 | 45433.6514 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Pareora Line Maintenance
230 |  | SKE1735 | TX B45 CCT3-60,61,63 The Avenue |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:35 | 45433.6493 | 0.78926 | 0.0018571 | 63 | 26775 | Planned | Planned interruption | Pareora Line Maintenance
231 |  | SKE1735 | Links L112-Links LL063-TX B45 |  | Normanby | 2024-05-21 08:30 | 45433.3542 | 2024-05-21 15:17 | 45433.6368 | 0.14397 | 0.00035373 | 12 | 4884 | Planned | Planned interruption | Pareora Line Maintenance
232 |  | GWM1160 | ABS G116 |  | Winchester | 2024-05-21 09:00 | 45433.375 | 2024-05-21 11:53 | 45433.4951 | 0.16829 | 0.00097276 | 33 | 5709 | Planned | Planned interruption | Tree cutting
233 |  | 4408 | F203 |  | Raincliff | 2024-05-21 10:54 | 45433.4542 | 2024-05-21 11:45 | 45433.4896 | 0.015034 | 0.00029478 | 10 | 510 | Unplanned | Defective equipment | Broken surge arrestor @ P#51963
234 |  | SKE1736 | Links L112-Links LL063-74,75,76,77,78,79,82,83 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:24 | 45434.6417 | 1.0129 | 0.0024466 | 83 | 34362 | Planned | Planned interruption | Pareora Line Maintenance
235 |  | SKE1736 | 74 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:38 | 45434.6514 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Pareora Line Maintenance
236 |  | SKE1736 | 75 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:41 | 45434.6535 | 0.012705 | 2.9478e-05 | 1 | 431 | Planned | Planned interruption | Pareora Line Maintenance
237 |  | SKE1736 | 76 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:40 | 45434.6528 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Pareora Line Maintenance
238 |  | SKE1736 | 77 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:42 | 45434.6542 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Pareora Line Maintenance
239 |  | SKE1736 | 78 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:41 | 45434.6535 | 0.012705 | 2.9478e-05 | 1 | 431 | Planned | Planned interruption | Pareora Line Maintenance
240 |  | SKE1736 | 79 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:48 | 45434.6583 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Pareora Line Maintenance
241 |  | SKE1736 | 82 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:32 | 45434.6472 | 0.01244 | 2.9478e-05 | 1 | 422 | Planned | Planned interruption | Pareora Line Maintenance
242 |  | SKE1736 | 83 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:36 | 45434.65 | 0.012557 | 2.9478e-05 | 1 | 426 | Planned | Planned interruption | Pareora Line Maintenance
243 |  | SKE1736 | 73 The Avenue |  | Normanby | 2024-05-22 08:30 | 45434.3542 | 2024-05-22 15:35 | 45434.6493 | 0.012528 | 2.9478e-05 | 1 | 425 | Planned | Planned interruption | Pareora Line Maintenance
244 |  | 5020 | Fuses W266 |  | Morven | 2024-05-23 19:00 | 45435.7917 | 2024-05-23 21:44 | 45435.9056 | 0.043509 | 0.0002653 | 9 | 1476 | Unplanned | Unknown | Unknown
245 |  | 5068 | W307 |  | Otaio | 2024-05-25 17:56 | 45437.7472 | 2024-05-25 19:37 | 45437.8174 | 0.020841 | 0.00020634 | 7 | 707 | Unplanned | Unknown | Unknown
246 |  | SKE1757 | TX D1705 |  | Temuka East | 2024-05-26 09:00 | 45438.375 | 2024-05-26 14:43 | 45438.6132 | 0.010111 | 2.9478e-05 | 1 | 343 | Planned | Planned interruption | Repair TX oil leak
247 |  | SKE1753 | TX B2119 CCT2 |  | Levels Plain | 2024-05-26 09:00 | 45438.375 | 2024-05-26 14:11 | 45438.591 | 0.091676 | 0.00029478 | 10 | 3110 | Planned | Planned interruption | TX Maintenance
248 |  | SKE1753 | TX B2119 CCT3 |  | Levels Plain | 2024-05-26 09:00 | 45438.375 | 2024-05-26 14:11 | 45438.591 | 0.055005 | 0.00017687 | 6 | 1866 | Planned | Planned interruption | TX Maintenance
249 |  | SKE1753 | TX B2119 CCT4 |  | Levels Plain | 2024-05-26 09:00 | 45438.375 | 2024-05-26 14:11 | 45438.591 | 0.0091676 | 2.9478e-05 | 1 | 311 | Planned | Planned interruption | TX Maintenance
250 |  | SKE1753 | TX B2119 ICP |  | Levels Plain | 2024-05-26 09:00 | 45438.375 | 2024-05-26 14:12 | 45438.5917 | 0.009197 | 2.9478e-05 | 1 | 312 | Planned | Planned interruption | TX Maintenance
251 |  | 5067 | W101 |  | Morven | 2024-05-26 17:52 | 45438.7444 | 2024-05-26 19:12 | 45438.8 | 0.018866 | 0.00023582 | 8 | 640 | Unplanned | Unknown | Unknown
252 |  | 5041 | W742 |  | Morven | 2024-05-27 06:32 | 45439.2722 | 2024-05-27 11:17 | 45439.4701 | 0.10921 | 0.00038321 | 13 | 3705 | Unplanned | Defective equipment | Broken Jumper @ Links W742
253 |  | 5041 | W291 - W653 - W742 |  | Morven | 2024-05-27 09:49 | 45439.409 | 2024-05-27 11:17 | 45439.4701 | 0.072633 | 0.00082537 | 28 | 2464 | Unplanned | Defective equipment | Broken Jumper @ Links W742
254 |  | HTR009 | ABS W482 |  | Morven | 2024-05-28 08:00 | 45440.3333 | 2024-05-28 16:19 | 45440.6799 | 0.29419 | 0.00058955 | 20 | 9980 | Planned | Planned interruption | Tree cutting
255 |  | SKE1738 | Links L112-Links LL063-60,61,63 The Avenue |  | Normanby | 2024-05-28 08:41 | 45440.3618 | 2024-05-28 13:07 | 45440.5465 | 0.20387 | 0.00076642 | 26 | 6916 | Planned | Planned interruption | Pareora Line Maintenance
256 |  | SKE1738 | 60 The Avenue |  | Normanby | 2024-05-28 08:41 | 45440.3618 | 2024-05-28 14:02 | 45440.5847 | 0.0094623 | 2.9478e-05 | 1 | 321 | Planned | Planned interruption | Pareora Line Maintenance
257 |  | SKE1738 | 61 The Avenue |  | Normanby | 2024-05-28 08:41 | 45440.3618 | 2024-05-28 14:01 | 45440.584 | 0.0094328 | 2.9478e-05 | 1 | 320 | Planned | Planned interruption | Pareora Line Maintenance
258 |  | SKE1738 | 63 The Avenue |  | Normanby | 2024-05-28 08:41 | 45440.3618 | 2024-05-28 13:15 | 45440.5521 | 0.0080769 | 2.9478e-05 | 1 | 274 | Planned | Planned interruption | Pareora Line Maintenance
259 |  | SKE1738 | TX B45 CCT3-60,61,63 The Avenue |  | Normanby | 2024-05-28 08:41 | 45440.3618 | 2024-05-28 13:13 | 45440.5507 | 0.50513 | 0.0018571 | 63 | 17136 | Planned | Planned interruption | Pareora Line Maintenance
260 |  | HTR007 | Fuses F145 |  | Cave | 2024-05-28 09:00 | 45440.375 | 2024-05-28 13:07 | 45440.5465 | 0.12378 | 0.00050112 | 17 | 4199 | Planned | Planned interruption | Tree cutting
261 |  | SKE1739 | Links L112-Links LL063-69,70,71,72,73,74,75,76,77,78 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 14:55 | 45441.6215 | 0.92336 | 0.0024172 | 82 | 31324 | Planned | Planned interruption | Pareora Line Maintenance
262 |  | SKE1739 | 69 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:08 | 45441.6306 | 0.011644 | 2.9478e-05 | 1 | 395 | Planned | Planned interruption | Pareora Line Maintenance
263 |  | SKE1739 | 70 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:09 | 45441.6312 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Pareora Line Maintenance
264 |  | SKE1739 | 71 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:12 | 45441.6333 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Pareora Line Maintenance
265 |  | SKE1739 | 72 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:10 | 45441.6319 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | Pareora Line Maintenance
266 |  | SKE1739 | 73 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:19 | 45441.6382 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Pareora Line Maintenance
267 |  | SKE1739 | 74 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:12 | 45441.6333 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Pareora Line Maintenance
268 |  | SKE1739 | 75 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:20 | 45441.6389 | 0.011997 | 2.9478e-05 | 1 | 407 | Planned | Planned interruption | Pareora Line Maintenance
269 |  | SKE1739 | 76 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:29 | 45441.6451 | 0.012263 | 2.9478e-05 | 1 | 416 | Planned | Planned interruption | Pareora Line Maintenance
270 |  | SKE1739 | 77 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:09 | 45441.6312 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Pareora Line Maintenance
271 |  | SKE1739 | 78 The Avenue |  | Normanby | 2024-05-29 08:33 | 45441.3562 | 2024-05-29 15:13 | 45441.634 | 0.011791 | 2.9478e-05 | 1 | 400 | Planned | Planned interruption | Pareora Line Maintenance
272 |  | SKE1751 | TX A1092 |  | Waihaorunga | 2024-05-29 09:02 | 45441.3764 | 2024-05-29 13:45 | 45441.5729 | 0.0083422 | 2.9478e-05 | 1 | 283 | Planned | Planned interruption | TX Maintenance
273 |  | 5121 | Fuses T317 to end |  | Waitohi | 2024-05-30 03:01 | 45442.1257 | 2024-05-30 04:30 | 45442.1875 | 0.047223 | 0.0005306 | 18 | 1602 | Unplanned | Unknown | Unknown - 1x Blown DO
274 |  | 5120 | Fuses T317 to end |  | Waitohi | 2024-05-30 06:22 | 45442.2653 | 2024-05-30 07:49 | 45442.3257 | 0.046162 | 0.0005306 | 18 | 1566 | Unplanned | Unknown | Unknown - 2x Blown DO's
275 |  | ACD134 | RMU L1130 FS-43,47,31,37,35,33,19,20,21,4,23,25,24,26 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 14:54 | 45443.6208 | 0.52924 | 0.0013854 | 47 | 17954 | Planned | Planned interruption | RMU Maintenance
276 |  | ACD134 | 43 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:42 | 45443.6542 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | RMU Maintenance
277 |  | ACD134 | 47 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:50 | 45443.6597 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | RMU Maintenance
278 |  | ACD134 | 31 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:03 | 45443.6271 | 0.011526 | 2.9478e-05 | 1 | 391 | Planned | Planned interruption | RMU Maintenance
279 |  | ACD134 | 37 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:08 | 45443.6306 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | RMU Maintenance
280 |  | ACD134 | 35 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:11 | 45443.6326 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | RMU Maintenance
281 |  | ACD134 | 33 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:15 | 45443.6354 | 0.011879 | 2.9478e-05 | 1 | 403 | Planned | Planned interruption | RMU Maintenance
282 |  | ACD134 | 19 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:04 | 45443.6278 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | RMU Maintenance
283 |  | ACD134 | 20 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:13 | 45443.634 | 0.011821 | 2.9478e-05 | 1 | 401 | Planned | Planned interruption | RMU Maintenance
284 |  | ACD134 | 21 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:09 | 45443.6312 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | RMU Maintenance
285 |  | ACD134 | 4 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:11 | 45443.6326 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | RMU Maintenance
286 |  | ACD134 | 23 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:04 | 45443.6278 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | RMU Maintenance
287 |  | ACD134 | 25 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:09 | 45443.6312 | 0.011703 | 2.9478e-05 | 1 | 397 | Planned | Planned interruption | RMU Maintenance
288 |  | ACD134 | 24 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:13 | 45443.634 | 0.011821 | 2.9478e-05 | 1 | 401 | Planned | Planned interruption | RMU Maintenance
289 |  | ACD134 | 26 Balmoral St |  | Highfield | 2024-05-31 08:32 | 45443.3556 | 2024-05-31 15:19 | 45443.6382 | 0.011997 | 2.9478e-05 | 1 | 407 | Planned | Planned interruption | RMU Maintenance
290 |  | SKE1756 | RMU R55 MS |  | Port Services | 2024-05-31 09:10 | 45443.3819 | 2024-05-31 14:19 | 45443.5965 | 0.0091086 | 2.9478e-05 | 1 | 309 | Planned | Planned interruption | TX Maintenance
291 |  | 5070 | Fuses TOC497 |  | Raincliff | 2024-05-31 10:00 | 45443.4167 | 2024-06-10 16:53 | 45453.7035 | 0.43665 | 2.9478e-05 | 1 | 14813 | Unplanned | Third party interference | Digger V Cable
292 |  | 3867 | CB M338 to end |  | Simons | 2024-06-01 06:19 | 45444.2632 | 2024-06-01 09:44 | 45444.4056 | 0.24172 | 0.0011791 | 40 | 8200 | Unplanned | Adverse weather | High Wind, Tree on line, Broken Conductor
293 |  | 3868 | Fuses F428 to end |  | Cave | 2024-06-01 08:27 | 45444.3521 | 2024-06-01 10:13 | 45444.4257 | 0.084365 | 0.0007959 | 27 | 2862 | Unplanned | Adverse weather | High Wind . Branch on line
294 |  | 3869 | TX Fuses TO A389 |  | Waikakahi | 2024-06-01 09:26 | 45444.3931 | 2024-06-01 11:16 | 45444.4694 | 0.0032425 | 2.9478e-05 | 1 | 110 | Unplanned | Adverse weather | High Wind
295 |  | 3871 | CB F138 to Links F140 |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 12:28 | 45444.5194 | 0.036552 | 0.00029478 | 10 | 1240 | Unplanned | Adverse weather | High Wind
296 |  | 3871 | Links F140 to Links F141 |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 12:51 | 45444.5354 | 0.069331 | 0.00047164 | 16 | 2352 | Unplanned | Adverse weather | High Wind
297 |  | 3871 | Links F141 to end minus F157 - F142 - F144 & F145 |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 13:35 | 45444.566 | 0.028151 | 0.00014739 | 5 | 955 | Unplanned | Adverse weather | High Wind
298 |  | 3871 | Fuses F157 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 13:46 | 45444.5736 | 0.047636 | 0.00023582 | 8 | 1616 | Unplanned | Adverse weather | High Wind
299 |  | 3871 | Fuses F145 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 13:42 | 45444.5708 | 0.099222 | 0.00050112 | 17 | 3366 | Unplanned | Adverse weather | High Wind
300 |  | 3871 | Links F144 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 13:40 | 45444.5694 | 0.14444 | 0.00073694 | 25 | 4900 | Unplanned | Adverse weather | High Wind
301 |  | 3871 | Links F142 to end minus F191 - F171 - F143 - F174 |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 15:05 | 45444.6285 | 0.091115 | 0.00032425 | 11 | 3091 | Unplanned | Adverse weather | High Wind
302 |  | 3871 | Fuses F191 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 15:12 | 45444.6333 | 0.033958 | 0.00011791 | 4 | 1152 | Unplanned | Adverse weather | High Wind
303 |  | 3871 | Fuses F171 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 15:20 | 45444.6389 | 0.026176 | 8.8433e-05 | 3 | 888 | Unplanned | Adverse weather | High Wind
304 |  | 3871 | Fuses F143 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 15:16 | 45444.6361 | 0.14633 | 0.00050112 | 17 | 4964 | Unplanned | Adverse weather | High Wind
305 |  | 3871 | Fuses F174 to end |  | Cave | 2024-06-01 10:24 | 45444.4333 | 2024-06-01 15:08 | 45444.6306 | 0.058602 | 0.00020634 | 7 | 1988 | Unplanned | Adverse weather | High Wind
306 |  | 3870 | CB W515 to end |  | Waikakahi | 2024-06-01 11:30 | 45444.4792 | 2024-06-01 11:37 | 45444.484 | 0.035697 | 0.0050996 | 173 | 1211 | Unplanned | Adverse weather | High wind - Bark removal
307 |  | 3871 | CB F138 to Links F140 |  | Cave | 2024-06-01 13:26 | 45444.5597 | 2024-06-01 13:35 | 45444.566 | 0.002653 | 0.00029478 | 10 | 90 | Unplanned | Adverse weather | High Wind
308 |  | 3871 | Links F140 to Links F141 |  | Cave | 2024-06-01 13:26 | 45444.5597 | 2024-06-01 13:35 | 45444.566 | 0.0042448 | 0.00047164 | 16 | 144 | Unplanned | Adverse weather | High Wind
309 |  | 4057 | Fuses L827 |  | Hadlow | 2024-06-01 14:29 | 45444.6035 | 2024-06-01 16:54 | 45444.7042 | 0.15815 | 0.0010907 | 37 | 5365 | Unplanned | Adverse weather | High Winds
310 |  | 3872 | PLP CB1 (Waitawa) to end |  | Waitawa | 2024-06-01 16:48 | 45444.7 | 2024-06-01 17:00 | 45444.7083 | 0.096569 | 0.0080474 | 273 | 3276 | Unplanned | Adverse weather | Emergency Trip to remove burning branch - Connells Rd
311 |  | 4309 | F138 to end less F142 |  | Cave | 2024-06-01 18:25 | 45444.7674 | 2024-06-01 19:46 | 45444.8236 | 0.1934 | 0.0023877 | 81 | 6561 | Unplanned | Adverse weather | Conductor on x arm #14053
312 |  | 4309 | F142 to end |  | Cave | 2024-06-01 18:25 | 45444.7674 | 2024-06-02 11:05 | 45445.4618 | 1.2381 | 0.0012381 | 42 | 42000 | Unplanned | Adverse weather | Conductor on x arm #14053
313 |  | 4308 | Fuses TO D404 to the end |  | Winchester | 2024-06-01 18:34 | 45444.7736 | 2024-06-02 | 45445 | 0.028829 | 8.8433e-05 | 3 | 978 | Unplanned | Adverse weather | Repair LV conductor beyond D404 Tx
314 |  | 4058 | ABS T306 |  | Waitohi | 2024-06-01 21:31 | 45444.8965 | 2024-06-01 21:46 | 45444.9069 | 0.021224 | 0.0014149 | 48 | 720 | Unplanned | Adverse weather | High Winds
315 |  | 4058 | TMK CB9-ABS T306 |  | Waitohi | 2024-06-01 21:31 | 45444.8965 | 2024-06-01 21:34 | 45444.8986 | 0.022727 | 0.0075758 | 257 | 771 | Unplanned | Adverse weather | High Winds
316 |  | ACD130 | ABS W174-TX A688 |  | Tawai | 2024-06-04 09:18 | 45447.3875 | 2024-06-04 16:11 | 45447.6743 | 0.23131 | 0.00056008 | 19 | 7847 | Planned | Planned interruption | TX Upgrade
317 |  | ACD130 | TX A688 |  | Tawai | 2024-06-04 09:18 | 45447.3875 | 2024-06-04 16:22 | 45447.6819 | 0.049994 | 0.00011791 | 4 | 1696 | Planned | Planned interruption | TX Upgrade
318 |  | ACD131 | ABS G107-Links G197- Pole 09047-TX D170 01 |  | Winchester | 2024-06-05 09:00 | 45448.375 | 2024-06-05 15:33 | 45448.6479 | 0.35913 | 0.00091381 | 31 | 12183 | Planned | Planned interruption | Red Tag Pole Replacement
319 |  | ACD131 | Pole 09047 |  | Winchester | 2024-06-05 09:00 | 45448.375 | 2024-06-05 16:18 | 45448.6792 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Red Tag Pole Replacement
320 |  | ACD131 | Pole 09032 |  | Winchester | 2024-06-05 09:00 | 45448.375 | 2024-06-05 16:35 | 45448.691 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Red Tag Pole Replacement
321 |  | ACD131 | Pole 09029 |  | Winchester | 2024-06-05 09:00 | 45448.375 | 2024-06-05 16:25 | 45448.684 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Red Tag Pole Replacement
322 |  | ACD131 | TX D170 01-Pole 09032- Pole 09029 |  | Winchester | 2024-06-05 09:00 | 45448.375 | 2024-06-05 15:50 | 45448.6597 | 0.20546 | 0.00050112 | 17 | 6970 | Planned | Planned interruption | Red Tag Pole Replacement
323 |  | JJV149 | Fuses F232 |  | Fairlie Rural | 2024-06-05 09:02 | 45448.3764 | 2024-06-05 13:15 | 45448.5521 | 0.49222 | 0.0019455 | 66 | 16698 | Planned | Planned interruption | New TX
324 |  | ACD143 | Fuses F179 |  | Fairlie Rural | 2024-06-07 09:00 | 45450.375 | 2024-06-07 11:09 | 45450.4646 | 0.019013 | 0.00014739 | 5 | 645 | Planned | Planned interruption | Pole Replacement
325 |  | 3801 | TMK CB9-ABS T313 |  | Waitohi | 2024-06-07 09:00 | 45450.375 | 2024-06-07 10:54 | 45450.4542 | 0.28564 | 0.0025056 | 85 | 9690 | Unplanned | Defective equipment | Repair broken jumper at ABS T306
326 |  | ACD144 | Fuses F108 |  | Cave | 2024-06-07 09:12 | 45450.3833 | 2024-06-07 11:57 | 45450.4979 | 0.0097276 | 5.8955e-05 | 2 | 330 | Planned | Planned interruption | Pole Replacement
327 |  | SKE1773 | DB C39 |  | Hayes Street | 2024-06-09 08:30 | 45452.3542 | 2024-06-09 16:27 | 45452.6854 | 0.042183 | 8.8433e-05 | 3 | 1431 | Planned | Planned interruption | TE12 UG Sub replacement
328 |  | SKE1773 | TE12 CCT16 |  | Hayes Street | 2024-06-09 08:30 | 45452.3542 | 2024-06-09 16:41 | 45452.6951 | 0.057894 | 0.00011791 | 4 | 1964 | Planned | Planned interruption | TE12 UG Sub replacement
329 |  | SKE1773 | TE12 CCT15 |  | Hayes Street | 2024-06-09 08:30 | 45452.3542 | 2024-06-09 16:49 | 45452.7007 | 0.14709 | 0.00029478 | 10 | 4990 | Planned | Planned interruption | TE12 UG Sub replacement
330 |  | JJV148 | TX B1775 |  | Redruth 2 | 2024-06-09 09:00 | 45452.375 | 2024-06-09 17:17 | 45452.7201 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | New TX & RMU
331 |  | JJV148 | ABS L283-Links L500-LV links LL084-TX B1775 |  | Redruth 2 | 2024-06-09 09:00 | 45452.375 | 2024-06-09 16:00 | 45452.6667 | 0.4457 | 0.0010612 | 36 | 15120 | Planned | Planned interruption | New TX & RMU
332 |  | OS KCK678 | CB W685 |  | Otaio | 2024-06-09 10:00 | 45452.4167 | 2024-06-09 10:04 | 45452.4194 | 0.0074284 | 0.0018571 | 63 | 252 | Planned | Planned interruption | Reconfiguring Network
333 |  | OS KCK678 | LB ABS W315-CB W685 |  | Otaio | 2024-06-09 10:02 | 45452.4181 | 2024-06-09 10:03 | 45452.4187 | 0.0010317 | 0.0010317 | 35 | 35 | Planned | Planned interruption | Reconfiguring Network
334 |  | ACD142 | ABS L878 |  | Normanby | 2024-06-10 09:00 | 45453.375 | 2024-06-10 15:03 | 45453.6271 | 0.19261 | 0.0005306 | 18 | 6534 | Planned | Planned interruption | Pole Replacement
335 |  | 5044 | F287 - F250 |  | Fairlie Rural | 2024-06-10 11:27 | 45453.4771 | 2024-06-10 12:19 | 45453.5132 | 0.26365 | 0.0050702 | 172 | 8944 | Unplanned | Unknown | Unknown
336 |  | 5044 | F250 - End |  | Fairlie Rural | 2024-06-10 11:27 | 45453.4771 | 2024-06-10 12:31 | 45453.5215 | 0.092442 | 0.0014444 | 49 | 3136 | Unplanned | Unknown | Unknown
337 |  | 3791 | CB G251 - T325 |  | Speechley | 2024-06-10 14:19 | 45453.5965 | 2024-06-10 15:22 | 45453.6403 | 0.23214 | 0.0036847 | 125 | 7875 | Unplanned | Third party interference | Truck with trees hit lines @ P#10490
338 |  | 3791 | T325 |  | Speechley | 2024-06-10 14:19 | 45453.5965 | 2024-06-10 18:32 | 45453.7722 | 0.13424 | 0.0005306 | 18 | 4554 | Unplanned | Third party interference | Truck with trees hit lines @ P#10490
339 |  | JDJ088 | ABS W560-Pole 43056 |  | Otaio | 2024-06-11 08:45 | 45454.3646 | 2024-06-11 14:12 | 45454.5917 | 0.11567 | 0.00035373 | 12 | 3924 | Planned | Planned interruption | Red Tag Pole Replacement
340 |  | JDJ088 | Pole 43056 |  | Otaio | 2024-06-11 08:45 | 45454.3646 | 2024-06-11 14:14 | 45454.5931 | 0.0096981 | 2.9478e-05 | 1 | 329 | Planned | Planned interruption | Red Tag Pole Replacement
341 |  | 5042 | F306 to end |  | Totara Valley | 2024-06-11 14:10 | 45454.5903 | 2024-06-11 15:13 | 45454.634 | 0.0055713 | 8.8433e-05 | 3 | 189 | Unplanned | Defective equipment | Tipped crossarm at pole #18247
342 |  | JDJ107 | TX D85 |  | Rangitata | 2024-06-12 09:54 | 45455.4125 | 2024-06-12 14:00 | 45455.5833 | 0.014503 | 5.8955e-05 | 2 | 492 | Planned | Planned interruption | Replace standoff insulator
343 |  | JDJ107UP | TX D85 |  | Rangitata | 2024-06-12 14:00 | 45455.5833 | 2024-06-14 16:05 | 45457.6701 | 0.17716 | 5.8955e-05 | 2 | 6010 | Unplanned | Defective equipment | Repair cable
344 |  | 5045 | L643 - L164 |  | Normanby | 2024-06-13 12:43 | 45456.5299 | 2024-06-13 13:16 | 45456.5528 | 0.10798 | 0.003272 | 111 | 3663 | Unplanned | Third party interference | Tree on line @ P#42035
345 |  | 5045 | L164 |  | Normanby | 2024-06-13 12:43 | 45456.5299 | 2024-06-13 18:19 | 45456.7632 | 0.12876 | 0.00038321 | 13 | 4368 | Unplanned | Third party interference | Tree on line @ P#42035
346 |  | 4410 | L243 |  | Waitawa | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 15:58 | 45459.6653 | 0.099045 | 0.0012381 | 42 | 3360 | Unplanned | Third party interference | Car v Pole #19581
347 |  | 4410 | L347 + L244 |  | Waitawa | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:07 | 45459.6715 | 0.26235 | 0.0029478 | 100 | 8900 | Unplanned | Third party interference | Car v Pole #19581
348 |  | 4410 | L211 - L347 |  | Waitawa | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:07 | 45459.6715 | 0.049847 | 0.00056008 | 19 | 1691 | Unplanned | Third party interference | Car v Pole #19581
349 |  | 4410 | PLP CB1 - L246 - L211 - L244 - L243 |  | Waitawa | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 19:18 | 45459.8042 | 0.89966 | 0.0032131 | 109 | 30520 | Unplanned | Third party interference | Car v Pole #19581
350 |  | 4410 | PLP CB2 - L240 |  | Sutherland | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:39 | 45459.6937 | 0.13911 | 0.0011496 | 39 | 4719 | Unplanned | Third party interference | Car v Pole #19581
351 |  | 4410 | L246 |  | Waitawa | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:42 | 45459.6958 | 0.010966 | 8.8433e-05 | 3 | 372 | Unplanned | Third party interference | Car v Pole #19581
352 |  | 4410 | PLP CB5 - L231 |  | Pleasant Point Township | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:42 | 45459.6958 | 0.73105 | 0.0058955 | 200 | 24800 | Unplanned | Third party interference | Car v Pole #19581
353 |  | 4410 | PLP CB4 - L232 |  | Totara Valley | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:46 | 45459.6986 | 0.84518 | 0.006603 | 224 | 28672 | Unplanned | Third party interference | Car v Pole #19581
354 |  | 4410 | L1239 - L820 |  | Sutherland | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:49 | 45459.7007 | 0.065647 | 0.00050112 | 17 | 2227 | Unplanned | Third party interference | Car v Pole #19581
355 |  | 4410 | L820 |  | Sutherland | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:49 | 45459.7007 | 0.038616 | 0.00029478 | 10 | 1310 | Unplanned | Third party interference | Car v Pole #19581
356 |  | 4410 | L240 - L1239 |  | Sutherland | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:49 | 45459.7007 | 0.22397 | 0.0017097 | 58 | 7598 | Unplanned | Third party interference | Car v Pole #19581
357 |  | 4410 | L232 - L109 |  | Totara Valley | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 17:09 | 45459.7146 | 1.1484 | 0.0076052 | 258 | 38958 | Unplanned | Third party interference | Car v Pole #19581
358 |  | 4410 | L109 |  | Totara Valley | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 17:44 | 45459.7389 | 0.52087 | 0.0028004 | 95 | 17670 | Unplanned | Third party interference | Car v Pole #19581
359 |  | 4410 | L1159 |  | Pleasant Point Township | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:57 | 45459.7063 | 0.23765 | 0.0017097 | 58 | 8062 | Unplanned | Third party interference | Car v Pole #19581
360 |  | 4410 | L231 - L1159 |  | Pleasant Point Township | 2024-06-16 14:38 | 45459.6097 | 2024-06-16 16:57 | 45459.7063 | 0.32779 | 0.0023582 | 80 | 11120 | Unplanned | Third party interference | Car v Pole #19581
361 |  | 4410 | PLP CB5 - L231 |  | Pleasant Point Township | 2024-06-16 17:17 | 45459.7201 | 2024-06-16 17:19 | 45459.7215 | 0.011791 | 0.0058955 | 200 | 400 | Unplanned | Third party interference | Car v Pole #19581
362 |  | 4410 | PLP CB5 - L231 |  | Pleasant Point Township | 2024-06-16 19:58 | 45459.8319 | 2024-06-16 20:01 | 45459.834 | 0.017687 | 0.0058955 | 200 | 600 | Unplanned | Third party interference | Car v Pole #19581
363 |  | 4410 | L1159 |  | Pleasant Point Township | 2024-06-16 19:58 | 45459.8319 | 2024-06-16 20:01 | 45459.834 | 0.0051291 | 0.0017097 | 58 | 174 | Unplanned | Third party interference | Car v Pole #19581
364 |  | 4410 | L231 - L1159 |  | Pleasant Point Township | 2024-06-16 19:58 | 45459.8319 | 2024-06-16 20:01 | 45459.834 | 0.0070746 | 0.0023582 | 80 | 240 | Unplanned | Third party interference | Car v Pole #19581
365 |  | 4410 | L1239 - L820 |  | Sutherland | 2024-06-16 20:25 | 45459.8507 | 2024-06-17 00:15 | 45460.0104 | 0.11526 | 0.00050112 | 17 | 3910 | Unplanned | Defective equipment | Faulty LB ABS L639
366 |  | 4410 | L820 |  | Sutherland | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 21:36 | 45459.9 | 0.020929 | 0.00029478 | 10 | 710 | Unplanned | Defective equipment | Faulty LB ABS L639
367 |  | 4410 | L240 - L1239 |  | Sutherland | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 20:40 | 45459.8611 | 0.025646 | 0.0017097 | 58 | 870 | Unplanned | Third party interference | Car v Pole #19581
368 |  | 4410 | L232 - L109 |  | Totara Valley | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 20:40 | 45459.8611 | 0.11408 | 0.0076052 | 258 | 3870 | Unplanned | Third party interference | Car v Pole #19581
369 |  | 4410 | CB2742 - F293 + F298 |  | Cave | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 21:12 | 45459.8833 | 0.51816 | 0.011025 | 374 | 17578 | Unplanned | Defective equipment | Faulty LB ABS L639
370 |  | 4410 | FX17 |  | Cave | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 21:59 | 45459.916 | 0.096981 | 0.0010317 | 35 | 3290 | Unplanned | Defective equipment | Faulty LB ABS L639
371 |  | 4410 | F293 - F298 - FX17 |  | Cave | 2024-06-16 20:25 | 45459.8507 | 2024-06-16 23:36 | 45459.9833 | 0.033781 | 0.00017687 | 6 | 1146 | Unplanned | Defective equipment | Faulty LB ABS L639
372 |  | 4410 | L109 |  | Totara Valley | 2024-06-16 21:48 | 45459.9083 | 2024-06-16 21:49 | 45459.909 | 0.0028004 | 0.0028004 | 95 | 95 | Unplanned | Third party interference | Car v Pole #19581
373 |  | 4410 | L211 - L347 |  | Waitawa | 2024-06-16 22:31 | 45459.9382 | 2024-06-16 22:34 | 45459.9403 | 0.0016802 | 0.00056008 | 19 | 57 | Unplanned | Third party interference | Car v Pole #19581
374 |  | 4410 | FX17 |  | Cave | 2024-06-17 | 45460 | 2024-06-17 00:03 | 45460.0021 | 0.0030952 | 0.0010317 | 35 | 105 | Unplanned | Defective equipment | Faulty LB ABS L639
375 |  | 4410 | L820 |  | Sutherland | 2024-06-17 00:18 | 45460.0125 | 2024-06-17 00:20 | 45460.0139 | 0.00058955 | 0.00029478 | 10 | 20 | Unplanned | Defective equipment | Faulty LB ABS L639
376 |  | 5139 | PAR CB6 - ABS L166 |  | Normanby | 2024-06-18 07:02 | 45461.2931 | 2024-06-18 08:29 | 45461.3535 | 0.91298 | 0.010494 | 356 | 30972 | Unplanned | Defective equipment | Broken ABS L166
377 |  | 5139 | ABS L145 |  | Normanby | 2024-06-18 07:02 | 45461.2931 | 2024-06-18 10:05 | 45461.4201 | 1.0303 | 0.0056302 | 191 | 34953 | Unplanned | Defective equipment | Broken ABS L166
378 |  | 5139 | ABS L878 |  | Normanby | 2024-06-18 07:02 | 45461.2931 | 2024-06-18 10:21 | 45461.4313 | 0.10559 | 0.0005306 | 18 | 3582 | Unplanned | Defective equipment | Broken ABS L166
379 |  | 5139 | ABS L166-ABS L145-L878 |  | Normanby | 2024-06-18 07:02 | 45461.2931 | 2024-06-18 13:09 | 45461.5479 | 0.06491 | 0.00017687 | 6 | 2202 | Unplanned | Defective equipment | Broken ABS L166
380 |  | 5139 | ABS L141-ABS L166 |  | Normanby | 2024-06-18 10:11 | 45461.4243 | 2024-06-18 13:11 | 45461.5493 | 0.068978 | 0.00038321 | 13 | 2340 | Unplanned | Defective equipment | Broken ABS L166
381 |  | HTR021 | Fuses G101 |  | Winchester | 2024-06-19 08:09 | 45462.3396 | 2024-06-19 13:05 | 45462.5451 | 0.20068 | 0.00067799 | 23 | 6808 | Planned | Planned interruption | Tree Trimming
382 |  | BDS001 | ABS F154-ABS F156-Pole 47950 |  | Cave | 2024-06-20 09:10 | 45463.3819 | 2024-06-20 17:45 | 45463.7396 | 0.68314 | 0.0013265 | 45 | 23175 | Planned | Planned interruption | ABY Maint
383 |  | BDS001 | Pole 47950 |  | Cave | 2024-06-20 09:10 | 45463.3819 | 2024-06-20 17:51 | 45463.7438 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | ABY Maint
384 |  | 5046 | TOA382 |  | Morven | 2024-06-21 13:20 | 45464.5556 | 2024-06-21 15:12 | 45464.6333 | 0.0033015 | 2.9478e-05 | 1 | 112 | Unplanned | Unknown | Blown fuse 11kV pole TOA382
385 |  | 5049 | CB L839 to End |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 15:14 | 45466.6347 | 0.96498 | 0.0073105 | 248 | 32736 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
386 |  | 5049 | L798 - L839 |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 15:14 | 45466.6347 | 0.015564 | 0.00011791 | 4 | 528 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
387 |  | 5049 | L812 to End |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 15:38 | 45466.6514 | 0.43686 | 0.0028004 | 95 | 14820 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
388 |  | 5049 | L799 - L812 |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 15:52 | 45466.6611 | 2.8564 | 0.016802 | 570 | 96900 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
389 |  | 5049 | Pole #35218 - L798 |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 23:38 | 45466.9847 | 0.18748 | 0.00029478 | 10 | 6360 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
390 |  | 5049 | Pole #35227 - L799 |  | Hadlow | 2024-06-23 13:02 | 45466.5431 | 2024-06-23 23:27 | 45466.9771 | 0.6264 | 0.0010022 | 34 | 21250 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
391 |  | 5049 | L812 to End (2) |  | Hadlow | 2024-06-23 17:40 | 45466.7361 | 2024-06-23 18:37 | 45466.7757 | 0.15962 | 0.0028004 | 95 | 5415 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
392 |  | 5049 | L798 - L839 (2) |  | Hadlow | 2024-06-23 23:35 | 45466.9826 | 2024-06-23 23:38 | 45466.9847 | 0.00035373 | 0.00011791 | 4 | 12 | Unplanned | Defective equipment | Blown Arrestors at Pole #35228
393 |  | 5122 | Pole #35288 to links L797 minus TX B2078 - B119 - B1588 |  | Hadlow | 2024-06-24 11:52 | 45467.4944 | 2024-06-24 17:10 | 45467.7153 | 0.037496 | 0.00011791 | 4 | 1272 | Unplanned | Unknown | Unknown
394 |  | 5122 | TX B2078 |  | Hadlow | 2024-06-24 11:52 | 45467.4944 | 2024-06-24 17:21 | 45467.7229 | 0.0096981 | 2.9478e-05 | 1 | 329 | Unplanned | Unknown | Unknown
395 |  | 5122 | TX B119 |  | Hadlow | 2024-06-24 11:52 | 45467.4944 | 2024-06-24 17:26 | 45467.7264 | 0.039382 | 0.00011791 | 4 | 1336 | Unplanned | Unknown | Unknown
396 |  | 5122 | TX B1588 |  | Hadlow | 2024-06-24 11:52 | 45467.4944 | 2024-06-24 17:30 | 45467.7292 | 0.0099634 | 2.9478e-05 | 1 | 338 | Unplanned | Unknown | Unknown
397 |  | 5047 | TOE208 |  | TEK-UHT 33kV | 2024-06-24 14:17 | 45467.5951 | 2024-06-24 14:42 | 45467.6125 | 0.0014739 | 5.8955e-05 | 2 | 50 | Unplanned | Defective equipment | Broken binder / tie @ P#21895
398 |  | 5122 | Pole #35288 to Links L286 |  | Hadlow | 2024-06-24 15:10 | 45467.6319 | 2024-06-24 17:10 | 45467.7153 | 0.12027 | 0.0010022 | 34 | 4080 | Unplanned | Unknown | Unknown
399 |  | HTR016 | Links G342 |  | Winchester | 2024-06-25 08:00 | 45468.3333 | 2024-06-25 13:21 | 45468.5563 | 0.0094623 | 2.9478e-05 | 1 | 321 | Planned | Planned interruption | Tree Trimming
400 |  | HTR016 | RMU G313 MS |  | Geraldine Township | 2024-06-25 08:00 | 45468.3333 | 2024-06-25 13:18 | 45468.5542 | 0.37496 | 0.0011791 | 40 | 12720 | Planned | Planned interruption | Tree Trimming
401 |  | BDS002 | ABS F154-ABS F156-17 Station St |  | Cave | 2024-06-25 08:36 | 45468.3583 | 2024-06-25 18:04 | 45468.7528 | 0.75345 | 0.0013265 | 45 | 25560 | Planned | Planned interruption | ABY Maint
402 |  | BDS002 | 17 Station St |  | Cave | 2024-06-25 08:36 | 45468.3583 | 2024-06-25 18:25 | 45468.7674 | 0.017362 | 2.9478e-05 | 1 | 589 | Planned | Planned interruption | ABY Maint
403 |  | HTR027 | Fuses T112 |  | Milford | 2024-06-25 09:00 | 45468.375 | 2024-06-25 10:33 | 45468.4396 | 0.052087 | 0.00056008 | 19 | 1767 | Planned | Planned interruption | Tree Trimming
404 |  | SKE1502 | ABS T690 |  | Rangitata | 2024-06-25 09:37 | 45468.4007 | 2024-06-25 13:01 | 45468.5424 | 0.01804 | 8.8433e-05 | 3 | 612 | Planned | Planned interruption | TX Maintenance
405 |  | HTR017 | ABS T497 |  | Rangitata Island | 2024-06-26 08:00 | 45469.3333 | 2024-06-26 14:29 | 45469.6035 | 0.72241 | 0.0018571 | 63 | 24507 | Planned | Planned interruption | Tree Trimming
406 |  | ACD153 | TX E207 |  | TEK-UHT 33kV | 2024-06-26 09:16 | 45469.3861 | 2024-06-26 16:28 | 45469.6861 | 0.050937 | 0.00011791 | 4 | 1728 | Planned | Planned interruption | Red Tag Pole replacements
407 |  | ACD153 | ABS M61-TX E207 |  | TEK-UHT 33kV | 2024-06-26 09:16 | 45469.3861 | 2024-06-26 16:07 | 45469.6715 | 0.18173 | 0.00044216 | 15 | 6165 | Planned | Planned interruption | Red Tag Pole replacements
408 |  | BDS003 | ABS F154-ABS F156-2 x ICPs |  | Cave | 2024-06-27 08:33 | 45470.3562 | 2024-06-27 14:45 | 45470.6146 | 0.48249 | 0.001297 | 44 | 16368 | Planned | Planned interruption | ABY Maint
409 |  | BDS003 | 2x ICPs |  | Cave | 2024-06-27 08:33 | 45470.3562 | 2024-06-27 14:54 | 45470.6208 | 0.022462 | 5.8955e-05 | 2 | 762 | Planned | Planned interruption | ABY Maint
410 |  | JMR676 | Beyond CB T626 Rolleston Rd |  | Rolleston Road | 2024-06-27 09:07 | 45470.3799 | 2024-06-27 10:33 | 45470.4396 | 0.47406 | 0.0055123 | 187 | 16082 | Unplanned | Wildlife | Swann found between poles #07207 & #51490
411 |  | JRM010 | TX D1286 |  | Mahan Road | 2024-06-27 09:28 | 45470.3944 | 2024-06-27 14:56 | 45470.6222 | 0.0096687 | 2.9478e-05 | 1 | 328 | Planned | Planned interruption | TX Repairs
412 |  | 3873 | Fuses L208 to end |  | Levels Plain | 2024-06-28 04:07 | 45471.1715 | 2024-06-28 06:23 | 45471.266 | 0.072161 | 0.0005306 | 18 | 2448 | Unplanned | Unknown | Blown DO's - Unknown
413 |  | 3874 | TMK CB2 to ABS T116 and T125 |  | Milford | 2024-06-28 06:00 | 45471.25 | 2024-06-28 07:27 | 45471.3104 | 0.17439 | 0.0020045 | 68 | 5916 | Unplanned | Wildlife | Conductors Down - Bird Strike
414 |  | 3874 | ABS T125 to end |  | Milford | 2024-06-28 06:00 | 45471.25 | 2024-06-28 07:37 | 45471.3174 | 0.26592 | 0.0027414 | 93 | 9021 | Unplanned | Wildlife | Conductors Down - Bird Strike
415 |  | 3874 | ABS T116 to fuses T119 |  | Milford | 2024-06-28 06:00 | 45471.25 | 2024-06-28 11:44 | 45471.4889 | 0.83151 | 0.0024172 | 82 | 28208 | Unplanned | Wildlife | Conductors Down - Bird Strike
416 |  | 3874 | Fuses T119 to end |  | Milford | 2024-06-28 06:00 | 45471.25 | 2024-06-28 08:09 | 45471.3396 | 0.12929 | 0.0010022 | 34 | 4386 | Unplanned | Wildlife | Conductors Down - Bird Strike
417 |  | 3875 | CB L839 to ABS L836 & ABS L834 |  | Hadlow | 2024-06-29 10:25 | 45472.434 | 2024-06-29 11:15 | 45472.4688 | 0.038321 | 0.00076642 | 26 | 1300 | Unplanned | Defective equipment | Faulty CB L839 Controller
418 |  | 3875 | ABS L834 to LBS L1401 |  | Hadlow | 2024-06-29 10:25 | 45472.434 | 2024-06-29 11:27 | 45472.4771 | 0.11331 | 0.0018276 | 62 | 3844 | Unplanned | Defective equipment | Faulty CB L839 Controller
419 |  | 3875 | LBS L1401 to end |  | Hadlow | 2024-06-29 10:25 | 45472.434 | 2024-06-29 11:29 | 45472.4785 | 0.20941 | 0.003272 | 111 | 7104 | Unplanned | Defective equipment | Faulty CB L839 Controller
420 |  | 3875 | ABS L836 to end |  | Hadlow | 2024-06-29 10:25 | 45472.434 | 2024-06-29 11:32 | 45472.4806 | 0.09875 | 0.0014739 | 50 | 3350 | Unplanned | Defective equipment | Faulty CB L839 Controller
421 |  | GWM1162 | ABS TX20 - ABS TX62 - Links T458 |  | Rangitata | 2024-07-01 09:24 | 45474.3917 | 2024-07-01 11:27 | 45474.4771 | 0.14503 | 0.0011791 | 40 | 4920 | Planned | Planned interruption | Tree Cutting
422 |  | HTR018 | T460 |  | Mahan Road | 2024-07-02 08:26 | 45475.3514 | 2024-07-02 15:27 | 45475.6438 | 0.2482 | 0.00058955 | 20 | 8420 | Planned | Planned interruption | Tree Cutting
423 |  | ACD145 | L601 - L1472 - 121, 123, 124 & 133 Luxmoore Rd |  | Grants Road | 2024-07-02 08:30 | 45475.3542 | 2024-07-02 14:23 | 45475.5993 | 0.31217 | 0.00088433 | 30 | 10590 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance
424 |  | ACD145 | 133 Luxmoore Road |  | Grants Road | 2024-07-02 08:30 | 45475.3542 | 2024-07-02 14:27 | 45475.6021 | 0.010524 | 2.9478e-05 | 1 | 357 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance
425 |  | ACD145 | 121 + 133 Luxmoore Road |  | Grants Road | 2024-07-02 08:30 | 45475.3542 | 2024-07-02 14:33 | 45475.6062 | 0.021401 | 5.8955e-05 | 2 | 726 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance
426 |  | ACD145 | 124 Luxmoore Road |  | Grants Road | 2024-07-02 08:30 | 45475.3542 | 2024-07-02 14:35 | 45475.6076 | 0.010759 | 2.9478e-05 | 1 | 365 | Planned | Planned interruption | Isolate & Earth ABS L601 for Maintenance
427 |  | HTR006 | Fuses F180 |  | Cave | 2024-07-02 09:00 | 45475.375 | 2024-07-02 14:48 | 45475.6167 | 0.071808 | 0.00020634 | 7 | 2436 | Planned | Planned interruption | Tree Cutting
428 |  | JRM017 | Fuses TO C423 |  | Fairlie Rural | 2024-07-02 09:49 | 45475.409 | 2024-07-02 14:47 | 45475.616 | 0.017569 | 5.8955e-05 | 2 | 596 | Planned | Planned interruption | Isolation for repairs to TX C423
429 |  | HTR030 | ABS F101 |  | Cave | 2024-07-03 08:00 | 45476.3333 | 2024-07-03 13:45 | 45476.5729 | 0.35594 | 0.0010317 | 35 | 12075 | Planned | Planned interruption | Tree Cutting
430 |  | 5048 | Fuses TO B731 to end |  | Hadlow | 2024-07-03 13:47 | 45476.5743 | 2024-07-03 14:27 | 45476.6021 | 0.0035373 | 8.8433e-05 | 3 | 120 | Unplanned | Wildlife | Remove birds Nests
431 |  | JMR672 | Fuses TO A705 |  | Tawai | 2024-07-08 10:00 | 45481.4167 | 2024-07-08 10:10 | 45481.4236 | 0.018866 | 0.0018866 | 64 | 640 | Planned | Planned interruption | Transformer Tap Change
432 |  | 5050 | W308 to end at pole #06007 |  | Otaio | 2024-07-09 14:57 | 45482.6229 | 2024-07-09 15:39 | 45482.6521 | 0.014857 | 0.00035373 | 12 | 504 | Unplanned | Defective equipment | Broken 11kV jumper at pole #06007
433 |  | 5123 | BPD CB13 to ABS W117, ABS W138 & ABS W133 |  | Waikakahi | 2024-07-11 01:58 | 45484.0819 | 2024-07-11 04:27 | 45484.1854 | 0.25475 | 0.0017097 | 58 | 8642 | Unplanned | Wildlife | Possum at pole #33049
434 |  | 5123 | ABS W133 to end |  | Waikakahi | 2024-07-11 01:58 | 45484.0819 | 2024-07-11 04:58 | 45484.2069 | 0.058366 | 0.00032425 | 11 | 1980 | Unplanned | Wildlife | Possum at pole #33049
435 |  | 5123 | ABS W138 to end |  | Waikakahi | 2024-07-11 01:58 | 45484.0819 | 2024-07-11 04:59 | 45484.2076 | 0.090703 | 0.00050112 | 17 | 3077 | Unplanned | Wildlife | Possum at pole #33049
436 |  | 5123 | ABS W117 to end |  | Waikakahi | 2024-07-11 01:58 | 45484.0819 | 2024-07-11 05:15 | 45484.2188 | 1.0801 | 0.0054828 | 186 | 36642 | Unplanned | Wildlife | Possum at pole #33049
437 |  | 3803 | Fuses TOD324 to end |  | Woodbury | 2024-07-11 12:06 | 45484.5042 | 2024-07-11 12:58 | 45484.5403 | 0.0015328 | 2.9478e-05 | 1 | 52 | Unplanned | Defective equipment | Broken insulator pole #51954
438 |  | 3804 | CB7 open to Q44 |  | Church Street South Side | 2024-07-12 11:41 | 45485.4868 | 2024-07-12 11:48 | 45485.4917 | 0.022079 | 0.0031541 | 107 | 749 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace
439 |  | 3804 | TE102-17 |  | Church Street South Side | 2024-07-12 11:41 | 45485.4868 | 2024-07-12 14:01 | 45485.584 | 0.1073 | 0.00076642 | 26 | 3640 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace
440 |  | 3804 | ICPs Q17 |  | Church Street South Side | 2024-07-12 11:41 | 45485.4868 | 2024-07-12 14:20 | 45485.5972 | 0.0093739 | 5.8955e-05 | 2 | 318 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace
441 |  | 3804 | CB7 to Q44 |  | Church Street South Side | 2024-07-12 13:54 | 45485.5792 | 2024-07-12 14:01 | 45485.584 | 0.022079 | 0.0031541 | 107 | 749 | Unplanned | Third party interference | UG sub isolate to open LV circuit for DB Q17 replace
442 |  | ACD137 | Pole 29730-L607-B694 CCT3-B203 CCT2-Pole 29757-B917-37, 28D Kent-50 Kelvin-19, 18, 20, 15 Kent |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:00 | 45488.6667 | 1.3132 | 0.0029183 | 99 | 44550 | Planned | Planned interruption | Lines Maintenance
443 |  | ACD137 | B917 CCT2-2 Usk St-6 Usk St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:05 | 45488.6701 | 0.54991 | 0.0012086 | 41 | 18655 | Planned | Planned interruption | Lines Maintenance
444 |  | ACD137 | 2 Usk St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:33 | 45488.6896 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Lines Maintenance
445 |  | ACD137 | 6 Usk St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 17:18 | 45488.7208 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance
446 |  | ACD137 | B917-B917 CCT2-87 Kent |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:11 | 45488.6743 | 0.23102 | 0.00050112 | 17 | 7837 | Planned | Planned interruption | Lines Maintenance
447 |  | ACD137 | 87 Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:38 | 45488.6931 | 0.014385 | 2.9478e-05 | 1 | 488 | Planned | Planned interruption | Lines Maintenance
448 |  | ACD137 | 37 Kent |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 17:06 | 45488.7125 | 0.01521 | 2.9478e-05 | 1 | 516 | Planned | Planned interruption | Lines Maintenance
449 |  | ACD137 | 28D Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:54 | 45488.7042 | 0.014857 | 2.9478e-05 | 1 | 504 | Planned | Planned interruption | Lines Maintenance
450 |  | ACD137 | 50 Kelvin St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 17:00 | 45488.7083 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Lines Maintenance
451 |  | ACD137 | 18 Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:42 | 45488.6958 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Lines Maintenance
452 |  | ACD137 | 19 Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 16:42 | 45488.6958 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Lines Maintenance
453 |  | ACD137 | 20 Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 17:18 | 45488.7208 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance
454 |  | ACD137 | 15 Kent St |  | Grants Road | 2024-07-15 08:30 | 45488.3542 | 2024-07-15 17:18 | 45488.7208 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Lines Maintenance
455 |  | GWM1167 | TX Fuses TO B1443 |  | Hadlow | 2024-07-15 09:00 | 45488.375 | 2024-07-15 15:42 | 45488.6542 | 0.0237 | 5.8955e-05 | 2 | 804 | Planned | Planned interruption | Tree cutting
456 |  | 3915 | Fuses TO A234 |  | Morven | 2024-07-15 15:38 | 45488.6514 | 2024-07-15 21:34 | 45488.8986 | 0.010494 | 2.9478e-05 | 1 | 356 | Unplanned | Third party interference | Truck vs Pole #32093
457 |  | ACD140 | TX B204-19,20,17,40,42,44,46,48,39,28,30,31 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:34 | 45489.6486 | 0.72491 | 0.0017097 | 58 | 24592 | Planned | Planned interruption | Line Maintenance
458 |  | ACD140 | 19 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:38 | 45489.6514 | 0.012616 | 2.9478e-05 | 1 | 428 | Planned | Planned interruption | Line Maintenance
459 |  | ACD140 | 20 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:42 | 45489.6542 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Maintenance
460 |  | ACD140 | 17 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:48 | 45489.6583 | 0.012911 | 2.9478e-05 | 1 | 438 | Planned | Planned interruption | Line Maintenance
461 |  | ACD140 | 40 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:45 | 45489.6562 | 0.012823 | 2.9478e-05 | 1 | 435 | Planned | Planned interruption | Line Maintenance
462 |  | ACD140 | 42 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:50 | 45489.6597 | 0.01297 | 2.9478e-05 | 1 | 440 | Planned | Planned interruption | Line Maintenance
463 |  | ACD140 | 44 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:51 | 45489.6604 | 0.013 | 2.9478e-05 | 1 | 441 | Planned | Planned interruption | Line Maintenance
464 |  | ACD140 | 46 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:39 | 45489.6521 | 0.012646 | 2.9478e-05 | 1 | 429 | Planned | Planned interruption | Line Maintenance
465 |  | ACD140 | 48 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:44 | 45489.6556 | 0.012793 | 2.9478e-05 | 1 | 434 | Planned | Planned interruption | Line Maintenance
466 |  | ACD140 | 39 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:36 | 45489.65 | 0.012557 | 2.9478e-05 | 1 | 426 | Planned | Planned interruption | Line Maintenance
467 |  | ACD140 | 28 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:46 | 45489.6569 | 0.012852 | 2.9478e-05 | 1 | 436 | Planned | Planned interruption | Line Maintenance
468 |  | ACD140 | 30 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:42 | 45489.6542 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Maintenance
469 |  | ACD140 | 31 Kelvin St |  | Grants Road | 2024-07-16 08:30 | 45489.3542 | 2024-07-16 15:52 | 45489.6611 | 0.013029 | 2.9478e-05 | 1 | 442 | Planned | Planned interruption | Line Maintenance
470 |  | ACD138A | 11kV Break Pole #29714-44,38,23,25,8 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 15:54 | 45490.6625 | 0.62823 | 0.0014149 | 48 | 21312 | Planned | Planned interruption | Line Maintenance
471 |  | ACD138A | LV Break Pole #29714-5,3,17 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 15:57 | 45490.6646 | 0.092236 | 0.00020634 | 7 | 3129 | Planned | Planned interruption | Line Maintenance
472 |  | ACD138A | 44 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 15:59 | 45490.666 | 0.013235 | 2.9478e-05 | 1 | 449 | Planned | Planned interruption | Line Maintenance
473 |  | ACD138A | 38 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:01 | 45490.6674 | 0.013294 | 2.9478e-05 | 1 | 451 | Planned | Planned interruption | Line Maintenance
474 |  | ACD138A | 23 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:03 | 45490.6687 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance
475 |  | ACD138A | 25 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:08 | 45490.6722 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Line Maintenance
476 |  | ACD138A | 8 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:02 | 45490.6681 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Line Maintenance
477 |  | ACD138A | 5 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:02 | 45490.6681 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Line Maintenance
478 |  | ACD138A | 3 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:00 | 45490.6667 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Line Maintenance
479 |  | ACD138A | 17 Arun St |  | Grants Road | 2024-07-17 08:30 | 45490.3542 | 2024-07-17 16:08 | 45490.6722 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Line Maintenance
480 |  | BDS004 | TX D1067-17.12,11,7 Church St-16 Burdon Rd |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:05 | 45490.6701 | 0.079413 | 0.00017687 | 6 | 2694 | Planned | Planned interruption | GLD Township Maintenance
481 |  | BDS004 | Fuses G161-20,14 Church-18,3 High St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:14 | 45490.6764 | 0.24301 | 0.0005306 | 18 | 8244 | Planned | Planned interruption | GLD Township Maintenance
482 |  | BDS004 | 20 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:37 | 45490.6924 | 0.014179 | 2.9478e-05 | 1 | 481 | Planned | Planned interruption | Lines Maintenance
483 |  | BDS004 | 14 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:49 | 45490.7007 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Lines Maintenance
484 |  | BDS004 | 18 High St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:24 | 45490.6833 | 0.013796 | 2.9478e-05 | 1 | 468 | Planned | Planned interruption | Lines Maintenance
485 |  | BDS004 | 17 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:50 | 45490.7014 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Lines Maintenance
486 |  | BDS004 | 12 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:40 | 45490.6944 | 0.014267 | 2.9478e-05 | 1 | 484 | Planned | Planned interruption | Lines Maintenance
487 |  | BDS004 | 11 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:45 | 45490.6979 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Lines Maintenance
488 |  | BDS004 | 3 High St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:55 | 45490.7049 | 0.014709 | 2.9478e-05 | 1 | 499 | Planned | Planned interruption | Lines Maintenance
489 |  | BDS004 | 7 Church St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:32 | 45490.6889 | 0.014031 | 2.9478e-05 | 1 | 476 | Planned | Planned interruption | Lines Maintenance
490 |  | BDS004 | 16 Burdon St |  | Woodbury | 2024-07-17 08:36 | 45490.3583 | 2024-07-17 16:40 | 45490.6944 | 0.014267 | 2.9478e-05 | 1 | 484 | Planned | Planned interruption | Lines Maintenance
491 |  | SKE1771 | Fuses L316-ABS L769 |  | Elginshire | 2024-07-17 09:02 | 45490.3764 | 2024-07-17 17:09 | 45490.7146 | 0.028711 | 5.8955e-05 | 2 | 974 | Planned | Planned interruption | TX Replacement / Upgrade
492 |  | SKE1771 | ABS L769 |  | Elginshire | 2024-07-17 09:02 | 45490.3764 | 2024-07-17 17:28 | 45490.7278 | 0.014916 | 2.9478e-05 | 1 | 506 | Planned | Planned interruption | TX Replacement / Upgrade
493 |  | ACD138B | 11kV Break Pole #29714-44A,52,50,48,35,41,39,35A,37,41A,45,47,43 Arun St-7,5,2,15,11 Killick Place |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 15:57 | 45491.6646 | 0.46118 | 0.0010317 | 35 | 15645 | Planned | Planned interruption | Line Maintenance
494 |  | ACD138B | 44A Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:03 | 45491.6687 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance
495 |  | ACD138B | 52 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:05 | 45491.6701 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Line Maintenance
496 |  | ACD138B | 50 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:10 | 45491.6736 | 0.01356 | 2.9478e-05 | 1 | 460 | Planned | Planned interruption | Line Maintenance
497 |  | ACD138B | 48 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:51 | 45491.7021 | 0.014768 | 2.9478e-05 | 1 | 501 | Planned | Planned interruption | Line Maintenance
498 |  | ACD138B | 35 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:21 | 45491.6813 | 0.013884 | 2.9478e-05 | 1 | 471 | Planned | Planned interruption | Line Maintenance
499 |  | ACD138B | 41 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:05 | 45491.6701 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Line Maintenance
500 |  | ACD138B | 39 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:16 | 45491.6778 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance
501 |  | ACD138B | 35A Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:22 | 45491.6819 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance
502 |  | ACD138B | 37 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:25 | 45491.684 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance
503 |  | ACD138B | 41A Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:30 | 45491.6875 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance
504 |  | ACD138B | 45 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:30 | 45491.6875 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance
505 |  | ACD138B | 47 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:25 | 45491.684 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance
506 |  | ACD138B | 43 Arun St |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:20 | 45491.6806 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance
507 |  | ACD138B | 7 Killick Pl |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:04 | 45491.6694 | 0.013383 | 2.9478e-05 | 1 | 454 | Planned | Planned interruption | Line Maintenance
508 |  | ACD138B | 5 Killick Pl |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:09 | 45491.6729 | 0.01353 | 2.9478e-05 | 1 | 459 | Planned | Planned interruption | Line Maintenance
509 |  | ACD138B | 2 Killick Pl |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:13 | 45491.6757 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance
510 |  | ACD138B | 15 Killick Pl |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:20 | 45491.6806 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance
511 |  | ACD138B | 11 Killick Pl |  | Grants Road | 2024-07-18 08:30 | 45491.3542 | 2024-07-18 16:25 | 45491.684 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance
512 |  | ACD138B | LV Break Pole #29714-11,9,10 Arun St |  | Grants Road | 2024-07-18 08:32 | 45491.3556 | 2024-07-18 15:59 | 45491.666 | 0.092236 | 0.00020634 | 7 | 3129 | Planned | Planned interruption | Line Maintenance
513 |  | ACD138B | 11 Arun St |  | Grants Road | 2024-07-18 08:32 | 45491.3556 | 2024-07-18 16:02 | 45491.6681 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Line Maintenance
514 |  | ACD138B | 9 Arun St |  | Grants Road | 2024-07-18 08:32 | 45491.3556 | 2024-07-18 16:05 | 45491.6701 | 0.013353 | 2.9478e-05 | 1 | 453 | Planned | Planned interruption | Line Maintenance
515 |  | ACD138B | 10 Arun St |  | Grants Road | 2024-07-18 08:32 | 45491.3556 | 2024-07-18 16:15 | 45491.6771 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance
516 |  | BDS005 | G326 to end - G154 to end |  | Woodbury | 2024-07-18 08:46 | 45491.3653 | 2024-07-18 17:37 | 45491.734 | 1.534 | 0.0028888 | 98 | 52038 | Planned | Planned interruption | Lines Maintenance
517 |  | SRT226 | Fuses TO C205 |  | Fairlie Rural | 2024-07-19 09:00 | 45492.375 | 2024-07-19 09:37 | 45492.4007 | 0.0010907 | 2.9478e-05 | 1 | 37 | Planned | Planned interruption | Pole Maintenance
518 |  | SKE1692 | TE31 |  | North Mole | 2024-07-21 08:26 | 45494.3514 | 2024-07-21 12:10 | 45494.5069 | 0.006603 | 2.9478e-05 | 1 | 224 | Planned | Planned interruption | RMU & TX Maintenance
519 |  | 5022 | Fuses TO D1391 |  | Geraldine Township | 2024-07-21 11:30 | 45494.4792 | 2024-07-21 16:36 | 45494.6917 | 0.0090202 | 2.9478e-05 | 1 | 306 | Unplanned | Third party interference | Digger Broke Conductor between Pole #35167 and Pole #35168
520 |  | 3805 | W461 to end |  | Morven | 2024-07-22 06:52 | 45495.2861 | 2024-07-22 09:40 | 45495.4028 | 0.0049522 | 2.9478e-05 | 1 | 168 | Unplanned | Wildlife | Broken conductor due to goose vs line
521 |  | 3805 | W742 to end - W461 to end |  | Morven | 2024-07-22 06:52 | 45495.2861 | 2024-07-22 09:35 | 45495.3993 | 0.057658 | 0.00035373 | 12 | 1956 | Unplanned | Wildlife | Broken conductor due to goose vs line
522 |  | 3809 | TX D1391 |  | Geraldine Township | 2024-07-22 11:09 | 45495.4646 | 2024-07-22 14:05 | 45495.5868 | 0.0051881 | 2.9478e-05 | 1 | 176 | Unplanned | Third party interference | Tractor V Pole
523 |  | 5140 | CB W103-ABS W461-TX A1154- TX A1157-TX A1158 |  | Morven | 2024-07-23 05:54 | 45496.2458 | 2024-07-23 13:50 | 45496.5764 | 0.12628 | 0.0002653 | 9 | 4284 | Unplanned | Wildlife | Goose V Lines
524 |  | 5140 | ABS W461 |  | Morven | 2024-07-23 05:54 | 45496.2458 | 2024-07-23 13:55 | 45496.5799 | 0.014179 | 2.9478e-05 | 1 | 481 | Unplanned | Wildlife | Goose V Lines
525 |  | 5140 | TX A1154 |  | Morven | 2024-07-23 05:54 | 45496.2458 | 2024-07-23 14:00 | 45496.5833 | 0.014326 | 2.9478e-05 | 1 | 486 | Unplanned | Wildlife | Goose V Lines
526 |  | 5140 | TX A1157 |  | Morven | 2024-07-23 05:54 | 45496.2458 | 2024-07-23 14:09 | 45496.5896 | 0.014591 | 2.9478e-05 | 1 | 495 | Unplanned | Wildlife | Goose V Lines
527 |  | 5140 | TX A1158 |  | Morven | 2024-07-23 05:54 | 45496.2458 | 2024-07-23 14:14 | 45496.5931 | 0.014739 | 2.9478e-05 | 1 | 500 | Unplanned | Wildlife | Goose V Lines
528 |  | ACD152 | TX B203 CCT2-84 & 86 Glen St |  | Grants Road | 2024-07-23 08:30 | 45496.3542 | 2024-07-23 16:45 | 45496.6979 | 0.23346 | 0.00047164 | 16 | 7920 | Planned | Planned interruption | Line Maintenance
529 |  | ACD152 | 84 Glen St |  | Grants Road | 2024-07-23 08:30 | 45496.3542 | 2024-07-23 16:50 | 45496.7014 | 0.014739 | 2.9478e-05 | 1 | 500 | Planned | Planned interruption | Line Maintenance
530 |  | ACD152 | 86 Glen St |  | Grants Road | 2024-07-23 08:30 | 45496.3542 | 2024-07-23 16:51 | 45496.7021 | 0.014768 | 2.9478e-05 | 1 | 501 | Planned | Planned interruption | Line Maintenance
531 |  | BDS006 | G152 to end - Tx D661 - 15 Burdon Rd - 16 Burdon Rd |  | Woodbury | 2024-07-23 08:40 | 45496.3611 | 2024-07-23 16:24 | 45496.6833 | 0.20516 | 0.00044216 | 15 | 6960 | Planned | Planned interruption | Lines Maintenance
532 |  | BDS006 | Tx D661 - 36 Burdon Rd |  | Woodbury | 2024-07-23 08:40 | 45496.3611 | 2024-07-23 16:35 | 45496.691 | 0.070009 | 0.00014739 | 5 | 2375 | Planned | Planned interruption | Lines Maintenance
533 |  | BDS006 | 36 Burdon Rd |  | Woodbury | 2024-07-23 08:40 | 45496.3611 | 2024-07-23 16:37 | 45496.6924 | 0.014061 | 2.9478e-05 | 1 | 477 | Planned | Planned interruption | Lines Maintenance
534 |  | BDS006 | 16 Burdon Rd |  | Woodbury | 2024-07-23 08:40 | 45496.3611 | 2024-07-23 16:38 | 45496.6931 | 0.01409 | 2.9478e-05 | 1 | 478 | Planned | Planned interruption | Lines Maintenance
535 |  | BDS006 | 15 Burdon Rd |  | Woodbury | 2024-07-23 08:40 | 45496.3611 | 2024-07-23 16:45 | 45496.6979 | 0.014297 | 2.9478e-05 | 1 | 485 | Planned | Planned interruption | Lines Maintenance
536 |  | ACD152 | TX B972-8,10,14,16,18 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:41 | 45496.6951 | 0.52243 | 0.0010907 | 37 | 17723 | Planned | Planned interruption | Line Maintenance
537 |  | ACD152 | 8 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:51 | 45496.7021 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Line Maintenance
538 |  | ACD152 | 10 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:53 | 45496.7035 | 0.014474 | 2.9478e-05 | 1 | 491 | Planned | Planned interruption | Line Maintenance
539 |  | ACD152 | 14 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:54 | 45496.7042 | 0.014503 | 2.9478e-05 | 1 | 492 | Planned | Planned interruption | Line Maintenance
540 |  | ACD152 | 16 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:57 | 45496.7063 | 0.014591 | 2.9478e-05 | 1 | 495 | Planned | Planned interruption | Line Maintenance
541 |  | ACD152 | 18 Ayr St |  | Grants Road | 2024-07-23 08:42 | 45496.3625 | 2024-07-23 16:55 | 45496.7049 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Line Maintenance
542 |  | PJD1605 | TX E356 CCT2-DB4461 |  | Tekapo | 2024-07-23 10:05 | 45496.4201 | 2024-07-23 13:37 | 45496.5674 | 0.062493 | 0.00029478 | 10 | 2120 | Planned | Planned interruption | TX Replacement / Upgrade
543 |  | PJD1605 | TX E356 CCT3 |  | Tekapo | 2024-07-23 10:05 | 45496.4201 | 2024-07-23 13:51 | 45496.5771 | 0.1399 | 0.00061903 | 21 | 4746 | Planned | Planned interruption | TX Replacement / Upgrade
544 |  | PJD1605 | TX E356 CCT4 |  | Tekapo | 2024-07-23 10:05 | 45496.4201 | 2024-07-23 14:16 | 45496.5944 | 0.096186 | 0.00038321 | 13 | 3263 | Planned | Planned interruption | TX Replacement / Upgrade
545 |  | PJD1605 | DB4461 |  | Tekapo | 2024-07-23 10:05 | 45496.4201 | 2024-07-23 13:47 | 45496.5743 | 0.006544 | 2.9478e-05 | 1 | 222 | Planned | Planned interruption | TX Replacement / Upgrade
546 |  | ACD155 | TX B972-31,40,38,51,49,25,21,17,20,24,16 Glen St-38,40 Athol Place-9,21,19 Ayr St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:13 | 45497.6757 | 0.35485 | 0.00076642 | 26 | 12038 | Planned | Planned interruption | Line Maintenance
547 |  | ACD155 | 31 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:16 | 45497.6778 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance
548 |  | ACD155 | 40 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:16 | 45497.6778 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance
549 |  | ACD155 | 38 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:19 | 45497.6799 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Line Maintenance
550 |  | ACD155 | 51 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:16 | 45497.6778 | 0.013737 | 2.9478e-05 | 1 | 466 | Planned | Planned interruption | Line Maintenance
551 |  | ACD155 | 49 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:20 | 45497.6806 | 0.013854 | 2.9478e-05 | 1 | 470 | Planned | Planned interruption | Line Maintenance
552 |  | ACD155 | 25 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:23 | 45497.6826 | 0.013943 | 2.9478e-05 | 1 | 473 | Planned | Planned interruption | Line Maintenance
553 |  | ACD155 | 21 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:33 | 45497.6896 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Line Maintenance
554 |  | ACD155 | 17 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:36 | 45497.6917 | 0.014326 | 2.9478e-05 | 1 | 486 | Planned | Planned interruption | Line Maintenance
555 |  | ACD155 | 20 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:43 | 45497.6965 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Line Maintenance
556 |  | ACD155 | 24 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:45 | 45497.6979 | 0.014591 | 2.9478e-05 | 1 | 495 | Planned | Planned interruption | Line Maintenance
557 |  | ACD155 | 16 Glen St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:50 | 45497.7014 | 0.014739 | 2.9478e-05 | 1 | 500 | Planned | Planned interruption | Line Maintenance
558 |  | ACD155 | 38 Athol Place |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:22 | 45497.6819 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance
559 |  | ACD155 | 40 Athol Place |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:30 | 45497.6875 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Line Maintenance
560 |  | ACD155 | 9 Ayr St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:48 | 45497.7 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Line Maintenance
561 |  | ACD155 | 21 Ayr St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:44 | 45497.6972 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Line Maintenance
562 |  | ACD155 | 19 Ayr St |  | Grants Road | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 16:56 | 45497.7056 | 0.014916 | 2.9478e-05 | 1 | 506 | Planned | Planned interruption | Line Maintenance
563 |  | HTR042 | Fuses W236-1 ICP |  | Glenavy | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 17:39 | 45497.7354 | 0.032366 | 5.8955e-05 | 2 | 1098 | Planned | Planned interruption | Tree cutting
564 |  | HTR042 | 1 ICP |  | Glenavy | 2024-07-24 08:30 | 45497.3542 | 2024-07-24 17:46 | 45497.7403 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | Tree cutting
565 |  | BDS007 | ABS G154-Fuses G326 |  | Woodbury | 2024-07-24 08:43 | 45497.3632 | 2024-07-24 15:54 | 45497.6625 | 1.2451 | 0.0028888 | 98 | 42238 | Planned | Planned interruption | Lines Maintenance
566 |  | BDS008 | Fuses G152-TX D890-TXD330-TX D1470-TX D1526 |  | Woodbury | 2024-07-25 08:31 | 45498.3549 | 2024-07-25 16:52 | 45498.7028 | 0.26583 | 0.0005306 | 18 | 9018 | Planned | Planned interruption | Lines Maintenance
567 |  | BDS008 | TX D890 |  | Woodbury | 2024-07-25 08:31 | 45498.3549 | 2024-07-25 16:59 | 45498.7076 | 0.029949 | 5.8955e-05 | 2 | 1016 | Planned | Planned interruption | Lines Maintenance
568 |  | BDS008 | TX D330 |  | Woodbury | 2024-07-25 08:31 | 45498.3549 | 2024-07-25 17:11 | 45498.716 | 0.015328 | 2.9478e-05 | 1 | 520 | Planned | Planned interruption | Lines Maintenance
569 |  | BDS008 | TX D1470 |  | Woodbury | 2024-07-25 08:31 | 45498.3549 | 2024-07-25 17:37 | 45498.734 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Lines Maintenance
570 |  | BDS008 | TX D1526 |  | Woodbury | 2024-07-25 08:31 | 45498.3549 | 2024-07-25 17:40 | 45498.7361 | 0.016183 | 2.9478e-05 | 1 | 549 | Planned | Planned interruption | Lines Maintenance
571 |  | 3807 | Beyond CB W590 |  | Tawai | 2024-07-26 10:52 | 45499.4528 | 2024-07-26 12:38 | 45499.5264 | 0.53744 | 0.0050702 | 172 | 18232 | Unplanned | Wildlife | Phase to Phase after Goose flew into lines
572 |  | 3807 | Beyond ABS W494 |  | Tawai | 2024-07-26 10:52 | 45499.4528 | 2024-07-26 13:56 | 45499.5806 | 0.499 | 0.0027119 | 92 | 16928 | Unplanned | Wildlife | Phase to Phase after Goose flew into lines
573 |  | 3876 | CB W664 to RMU W699 |  | Waihaorunga | 2024-07-28 04:21 | 45501.1813 | 2024-07-28 04:57 | 45501.2063 | 0.83728 | 0.023258 | 789 | 28404 | Unplanned | Wildlife | Possum at pole #20944
574 |  | 3876 | RMU W699 to end |  | Waihaorunga | 2024-07-28 04:21 | 45501.1813 | 2024-07-28 06:30 | 45501.2708 | 0.038026 | 0.00029478 | 10 | 1290 | Unplanned | Wildlife | Possum at pole #20944
575 |  | 4414 | PAR CB6 to end - L162 |  | Normanby | 2024-07-28 14:36 | 45501.6083 | 2024-07-28 15:30 | 45501.6458 | 0.86116 | 0.015947 | 541 | 29214 | Unplanned | Third party interference | Tree on line @ Tx B1417 caused by farmer cutting trees
576 |  | 4414 | L162 |  | Normanby | 2024-07-28 14:36 | 45501.6083 | 2024-07-28 17:50 | 45501.7431 | 0.17156 | 0.00088433 | 30 | 5820 | Unplanned | Third party interference | Tree on line @ Tx B1417 caused by farmer cutting trees
577 |  | ACD157 | ABS F273 |  | Fairlie Rural | 2024-07-29 08:40 | 45502.3611 | 2024-07-29 08:44 | 45502.3639 | 0.0018866 | 0.00047164 | 16 | 64 | Planned | Planned interruption | Pole Replacement
578 |  | ACD156 | D335-02-5 Darby St |  | Geraldine Township | 2024-07-29 09:00 | 45502.375 | 2024-07-29 18:37 | 45502.7757 | 0.085043 | 0.00014739 | 5 | 2885 | Planned | Planned interruption | TX Replacement
579 |  | ACD156 | D335-03-27 Hewlings St |  | Geraldine Township | 2024-07-29 09:00 | 45502.375 | 2024-07-29 19:04 | 45502.7944 | 0.28487 | 0.00047164 | 16 | 9664 | Planned | Planned interruption | TX Replacement
580 |  | ACD156 | 5 Darby St |  | Geraldine Township | 2024-07-29 09:00 | 45502.375 | 2024-07-29 19:04 | 45502.7944 | 0.017805 | 2.9478e-05 | 1 | 604 | Planned | Planned interruption | TX Replacement
581 |  | ACD156 | 27 Hewlings St |  | Geraldine Township | 2024-07-29 09:00 | 45502.375 | 2024-07-29 19:26 | 45502.8097 | 0.018453 | 2.9478e-05 | 1 | 626 | Planned | Planned interruption | TX Replacement
582 |  | ACD156 | D335-04 |  | Geraldine Township | 2024-07-29 09:00 | 45502.375 | 2024-07-29 18:41 | 45502.7785 | 0.30828 | 0.0005306 | 18 | 10458 | Planned | Planned interruption | TX Replacement
583 |  | ACD157 | ABS F255-ABS F277-ABS F273-TX C291 |  | Fairlie Rural | 2024-07-29 09:03 | 45502.3771 | 2024-07-29 14:07 | 45502.5882 | 0.21507 | 0.00070746 | 24 | 7296 | Planned | Planned interruption | Pole Replacement
584 |  | ACD157 | TX C291 |  | Fairlie Rural | 2024-07-29 09:03 | 45502.3771 | 2024-07-29 14:48 | 45502.6167 | 0.01017 | 2.9478e-05 | 1 | 345 | Planned | Planned interruption | Pole Replacement
585 |  | 3806 | Beyond F284 |  | Fairlie Rural | 2024-07-29 13:02 | 45502.5431 | 2024-07-29 13:57 | 45502.5813 | 0.0064851 | 0.00011791 | 4 | 220 | Unplanned | Defective equipment | Broken binder wire & insulator at pole #10742 & pole #10743
586 |  | ACD157 | ABS F273 |  | Fairlie Rural | 2024-07-29 14:35 | 45502.6076 | 2024-07-29 14:41 | 45502.6118 | 0.0028299 | 0.00047164 | 16 | 96 | Planned | Planned interruption | Pole Replacement
587 |  | JJV151 | TE140 CCT17 |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-29 18:30 | 45502.7708 | 0.0011791 | 0.00011791 | 4 | 40 | Planned | Planned interruption | Lucy Box replacement
588 |  | JJV151 | TE140 CCT15-LB H24 to H253 |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-29 18:41 | 45502.7785 | 0.0018571 | 8.8433e-05 | 3 | 63 | Planned | Planned interruption | Lucy Box replacement
589 |  | JJV151 | TE140 CCT16 |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-29 19:19 | 45502.8049 | 0.012174 | 0.00020634 | 7 | 413 | Planned | Planned interruption | Lucy Box replacement
590 |  | JJV151 | TE140 CCT14 |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-29 19:19 | 45502.8049 | 0.0052175 | 8.8433e-05 | 3 | 177 | Planned | Planned interruption | Lucy Box replacement
591 |  | JJV151 | TE140 CCT18-H337 CCT1-26 Canon St (2 ICPs) - 32 Canon St - 79 Sophia St |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-30 06:19 | 45503.2632 | 0.042389 | 5.8955e-05 | 2 | 1438 | Planned | Planned interruption | Lucy Box replacement
592 |  | JJV151 | 26 Canon St |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-30 08:00 | 45503.3333 | 0.048343 | 5.8955e-05 | 2 | 1640 | Planned | Planned interruption | Lucy Box replacement
593 |  | JJV151 | 32 Canon St |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-30 08:20 | 45503.3472 | 0.024761 | 2.9478e-05 | 1 | 840 | Planned | Planned interruption | Lucy Box replacement
594 |  | JJV151 | 79 Sophia St |  | Le Cren Street | 2024-07-29 18:20 | 45502.7639 | 2024-07-30 08:10 | 45503.3403 | 0.024466 | 2.9478e-05 | 1 | 830 | Planned | Planned interruption | Lucy Box replacement
595 |  | JJV151 | TE140 CCT15-LB H24 to H253 |  | Le Cren Street | 2024-07-29 18:56 | 45502.7889 | 2024-07-29 19:03 | 45502.7937 | 0.00061903 | 8.8433e-05 | 3 | 21 | Planned | Planned interruption | Lucy Box replacement
596 |  | JJV151 | TE140 CCT16 |  | Le Cren Street | 2024-07-30 06:00 | 45503.25 | 2024-07-30 06:19 | 45503.2632 | 0.0039205 | 0.00020634 | 7 | 133 | Planned | Planned interruption | Lucy Box replacement
597 |  | JJV151 | TE140 CCT14 |  | Le Cren Street | 2024-07-30 06:00 | 45503.25 | 2024-07-30 06:19 | 45503.2632 | 0.0016802 | 8.8433e-05 | 3 | 57 | Planned | Planned interruption | Lucy Box replacement
598 |  | JJV151 | TE140 CCT17 |  | Le Cren Street | 2024-07-30 06:02 | 45503.2514 | 2024-07-30 06:19 | 45503.2632 | 0.0020045 | 0.00011791 | 4 | 68 | Planned | Planned interruption | Lucy Box replacement
599 |  | RAK147 | ABS L817 |  | Hadlow | 2024-07-31 09:00 | 45504.375 | 2024-07-31 14:24 | 45504.6 | 0.31518 | 0.00097276 | 33 | 10692 | Planned | Planned interruption | New ABS and removal of fuses L819
600 |  | RAK146 | Links L286-ABS L802 |  | Hadlow | 2024-07-31 09:17 | 45504.3868 | 2024-07-31 12:40 | 45504.5278 | 0.053856 | 0.0002653 | 9 | 1827 | Planned | Planned interruption | CB L287 Settings changes
601 |  | PJD1623 | Fuses B1078 cct 06 |  | Highfield | 2024-08-01 09:00 | 45505.375 | 2024-08-01 13:05 | 45505.5451 | 0.057776 | 0.00023582 | 8 | 1960 | Planned | Planned interruption | DB Replacement
602 |  | PJD1623 | Fuses B1078 cct 05 |  | Highfield | 2024-08-01 09:02 | 45505.3764 | 2024-08-01 13:03 | 45505.5437 | 0.099458 | 0.00041269 | 14 | 3374 | Planned | Planned interruption | DB Replacement
603 |  | PJD1623 | Fuses B1078 cct 03 |  | Highfield | 2024-08-01 09:03 | 45505.3771 | 2024-08-01 13:02 | 45505.5431 | 0.17613 | 0.00073694 | 25 | 5975 | Planned | Planned interruption | DB Replacement
604 |  | PJD1623 | LB458 cct 04 |  | Highfield | 2024-08-01 09:14 | 45505.3847 | 2024-08-01 13:11 | 45505.5493 | 0.069862 | 0.00029478 | 10 | 2370 | Planned | Planned interruption | DB Replacement
605 |  | PJD1623 | DB2845 |  | Highfield | 2024-08-01 09:14 | 45505.3847 | 2024-08-01 13:44 | 45505.5722 | 0.023877 | 8.8433e-05 | 3 | 810 | Planned | Planned interruption | DB Replacement
606 |  | PJD1623 | CB B899 cct 03 - LB458 cct 04 - DB2845 |  | Highfield | 2024-08-01 09:14 | 45505.3847 | 2024-08-01 13:15 | 45505.5521 | 0.078145 | 0.00032425 | 11 | 2651 | Planned | Planned interruption | DB Replacement
607 |  | PJD1623 | CB B899 cct 02 |  | Highfield | 2024-08-01 09:17 | 45505.3868 | 2024-08-01 12:51 | 45505.5354 | 0.2334 | 0.0010907 | 37 | 7918 | Planned | Planned interruption | DB Replacement
608 |  | PJD1623 | CB B899 cct 04 |  | Highfield | 2024-08-01 09:17 | 45505.3868 | 2024-08-01 12:51 | 45505.5354 | 0.018925 | 8.8433e-05 | 3 | 642 | Planned | Planned interruption | DB Replacement
609 |  | PJD1625 | Beyond ABS L328 |  | Arowhenua | 2024-08-01 17:05 | 45505.7118 | 2024-08-01 18:31 | 45505.7715 | 0.020281 | 0.00023582 | 8 | 688 | Unplanned | Defective equipment | Broken binder wire & insulator at pole #35549
610 |  | ACD158 | F295 to End |  | Cave | 2024-08-05 08:08 | 45509.3389 | 2024-08-05 08:11 | 45509.341 | 0.0029183 | 0.00097276 | 33 | 99 | Planned | Planned interruption | Albury Maintenance
611 |  | ACD158 | ABS FX17 |  | Cave | 2024-08-05 08:09 | 45509.3396 | 2024-08-05 08:27 | 45509.3521 | 0.0010612 | 5.8955e-05 | 2 | 36 | Planned | Planned interruption | Albury Maintenance
612 |  | ACD158 | LB ABS F293 |  | Cave | 2024-08-05 08:30 | 45509.3542 | 2024-08-05 16:13 | 45509.6757 | 0.027296 | 5.8955e-05 | 2 | 926 | Planned | Planned interruption | Albury Maintenance
613 |  | ACD158 | TX B1963 |  | Cave | 2024-08-05 08:30 | 45509.3542 | 2024-08-05 16:48 | 45509.7 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Albury Maintenance
614 |  | ACD158 | TX B1957 |  | Cave | 2024-08-05 08:30 | 45509.3542 | 2024-08-05 16:47 | 45509.6993 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | Albury Maintenance
615 |  | ACD158 | TX B1263 |  | Cave | 2024-08-05 08:30 | 45509.3542 | 2024-08-05 16:46 | 45509.6986 | 0.014621 | 2.9478e-05 | 1 | 496 | Planned | Planned interruption | Albury Maintenance
616 |  | ACD158 | TX B1704 |  | Cave | 2024-08-05 08:30 | 45509.3542 | 2024-08-05 16:43 | 45509.6965 | 0.014532 | 2.9478e-05 | 1 | 493 | Planned | Planned interruption | Albury Maintenance
617 |  | ACD158 | ABS L1239 |  | Sutherland | 2024-08-05 08:32 | 45509.3556 | 2024-08-05 16:13 | 45509.6757 | 0.23102 | 0.00050112 | 17 | 7837 | Planned | Planned interruption | Albury Maintenance
618 |  | ACD159 | F298 - TOB1034 - TOB1033 - B335'01' |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 16:47 | 45510.6993 | 1.9659 | 0.0039795 | 135 | 66690 | Planned | Planned interruption | Lines Maintenance
619 |  | ACD159 | B335 '01' |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 16:54 | 45510.7042 | 0.59073 | 0.0011791 | 40 | 20040 | Planned | Planned interruption | Lines Maintenance
620 |  | ACD159 | Fuses TOB1034 |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 16:52 | 45510.7028 | 0.10297 | 0.00020634 | 7 | 3493 | Planned | Planned interruption | Lines Maintenance
621 |  | ACD159 | Fuses TOB1033 |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 17:11 | 45510.716 | 0.030539 | 5.8955e-05 | 2 | 1036 | Planned | Planned interruption | Lines Maintenance
622 |  | ACD159 | 20 Charles St |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 17:01 | 45510.709 | 0.014975 | 2.9478e-05 | 1 | 508 | Planned | Planned interruption | Lines Maintenance
623 |  | ACD159 | 28 Charles St |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 16:58 | 45510.7069 | 0.014886 | 2.9478e-05 | 1 | 505 | Planned | Planned interruption | Lines Maintenance
624 |  | ACD159 | 1383 SH8 Albury Cave Road |  | Cave | 2024-08-06 08:33 | 45510.3562 | 2024-08-06 17:03 | 45510.7104 | 0.015034 | 2.9478e-05 | 1 | 510 | Planned | Planned interruption | Lines Maintenance
625 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 15:41 | 45510.6535 | 0.27187 | 0.00067799 | 23 | 9223 | Planned | Planned interruption | RMU & TX Maintenance
626 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 15:53 | 45510.6618 | 0.048697 | 0.00011791 | 4 | 1652 | Planned | Planned interruption | RMU & TX Maintenance
627 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 16:03 | 45510.6687 | 0.22444 | 0.0005306 | 18 | 7614 | Planned | Planned interruption | RMU & TX Maintenance
628 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 16:14 | 45510.6764 | 0.29425 | 0.00067799 | 23 | 9982 | Planned | Planned interruption | RMU & TX Maintenance
629 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 16:19 | 45510.6799 | 0.18117 | 0.00041269 | 14 | 6146 | Planned | Planned interruption | RMU & TX Maintenance
630 |  | SKE1741 | TX TE72 |  | June Street | 2024-08-06 09:00 | 45510.375 | 2024-08-06 16:28 | 45510.6861 | 0.13206 | 0.00029478 | 10 | 4480 | Planned | Planned interruption | RMU & TX Maintenance
631 |  | ACD159 | LB ABSF293 - ABS F298 |  | Cave | 2024-08-06 17:34 | 45510.7319 | 2024-08-06 17:36 | 45510.7333 | 0.0024172 | 0.0012086 | 41 | 82 | Planned | Planned interruption | Lines Maintenance
632 |  | ACD160 | Fuses F136 |  | Cave | 2024-08-07 08:30 | 45511.3542 | 2024-08-07 16:05 | 45511.6701 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Pole Replacement
633 |  | ACD160 | Fuses F136 |  | Cave | 2024-08-07 08:30 | 45511.3542 | 2024-08-07 16:07 | 45511.6715 | 0.013471 | 2.9478e-05 | 1 | 457 | Planned | Planned interruption | Pole Replacement
634 |  | ACD160 | Fuses F136 |  | Cave | 2024-08-07 08:30 | 45511.3542 | 2024-08-07 16:30 | 45511.6875 | 0.014149 | 2.9478e-05 | 1 | 480 | Planned | Planned interruption | Pole Replacement
635 |  | ACD160 | Fuses F136 |  | Cave | 2024-08-07 08:30 | 45511.3542 | 2024-08-07 16:40 | 45511.6944 | 0.014444 | 2.9478e-05 | 1 | 490 | Planned | Planned interruption | Pole Replacement
636 |  | ACD160 | Fuses F136 |  | Cave | 2024-08-07 08:30 | 45511.3542 | 2024-08-07 15:55 | 45511.6632 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Pole Replacement
637 |  | ACD161 | TX B1034 |  | Cave | 2024-08-08 09:15 | 45512.3854 | 2024-08-08 11:50 | 45512.4931 | 0.027414 | 0.00017687 | 6 | 930 | Planned | Planned interruption | Pole Replacement
638 |  | ACD161 | TX B1034 |  | Cave | 2024-08-08 09:15 | 45512.3854 | 2024-08-08 11:51 | 45512.4938 | 0.0045985 | 2.9478e-05 | 1 | 156 | Planned | Planned interruption | Pole Replacement
639 |  | ACD161 | TX B1034 |  | Cave | 2024-08-08 09:15 | 45512.3854 | 2024-08-08 11:56 | 45512.4972 | 0.0047459 | 2.9478e-05 | 1 | 161 | Planned | Planned interruption | Pole Replacement
640 |  | ACD162 | TX B1673 |  | Cave | 2024-08-08 09:20 | 45512.3889 | 2024-08-08 12:27 | 45512.5188 | 0.0055123 | 2.9478e-05 | 1 | 187 | Planned | Planned interruption | Pole Replacement
641 |  | SKE1831 | TX E224 |  | Urban #2 | 2024-08-09 09:00 | 45513.375 | 2024-08-09 16:00 | 45513.6667 | 0.049522 | 0.00011791 | 4 | 1680 | Planned | Planned interruption | RMU & TX Maintenanace
642 |  | SKE1831 | TX E223 |  | Urban #2 | 2024-08-09 09:00 | 45513.375 | 2024-08-09 15:55 | 45513.6632 | 0.061166 | 0.00014739 | 5 | 2075 | Planned | Planned interruption | RMU & TX Maintenance
643 |  | SKE1831 | TX E222 |  | Urban #2 | 2024-08-09 09:00 | 45513.375 | 2024-08-09 15:50 | 45513.6597 | 0.048343 | 0.00011791 | 4 | 1640 | Planned | Planned interruption | RMU & TX Maintenance
644 |  | SKE1831 | TX E187 |  | Urban #2 | 2024-08-09 09:00 | 45513.375 | 2024-08-09 16:15 | 45513.6771 | 0.025646 | 5.8955e-05 | 2 | 870 | Planned | Planned interruption | RMU & TX Maintenance
645 |  | SKE1831 | TX E149 |  | Urban #2 | 2024-08-09 09:00 | 45513.375 | 2024-08-09 16:21 | 45513.6813 | 0.025999 | 5.8955e-05 | 2 | 882 | Planned | Planned interruption | RMU & TX Maintenance
646 |  | SRT240 | TX B373 |  | Hadlow | 2024-08-09 09:00 | 45513.375 | 2024-08-09 13:58 | 45513.5819 | 0.0087843 | 2.9478e-05 | 1 | 298 | Planned | Planned interruption | TX Upgrade
647 |  | 3811 | Orakipaoa Island Road Fuse T122 |  | Milford | 2024-08-09 09:06 | 45513.3792 | 2024-08-09 10:11 | 45513.4243 | 0.028741 | 0.00044216 | 15 | 975 | Unplanned | Unknown | Unknown
648 |  | 3877 | CB L1220 to end minus ABS L156 |  | Normanby | 2024-08-10 10:04 | 45514.4194 | 2024-08-10 11:57 | 45514.4979 | 0.25982 | 0.0022993 | 78 | 8814 | Unplanned | Third party interference | Digger VS Lines
649 |  | 3877 | ABS L156 to end |  | Normanby | 2024-08-10 10:04 | 45514.4194 | 2024-08-10 13:59 | 45514.5826 | 0.33251 | 0.0014149 | 48 | 11280 | Unplanned | Third party interference | Digger VS Lines
650 |  | SEM014 | Fuses W510 |  | Ikawai | 2024-08-12 10:04 | 45516.4194 | 2024-08-12 11:19 | 45516.4715 | 0.019897 | 0.0002653 | 9 | 675 | Unplanned | Defective equipment | Missing nuts on Insulator
651 |  | 4718 | CB L876 (Racecourse Rd) |  | Levels Plain | 2024-08-12 11:01 | 45516.459 | 2024-08-12 11:46 | 45516.4903 | 0.23744 | 0.0052765 | 179 | 8055 | Unplanned | Vegetation | Tree fell on lines
652 |  | 4718 | Fuses L195 |  | Levels Plain | 2024-08-12 11:01 | 45516.459 | 2024-08-12 14:25 | 45516.6007 | 0.030067 | 0.00014739 | 5 | 1020 | Unplanned | Vegetation | Tree fell on lines
653 |  | 4719 | CB F107 (Totara Valley Rd) |  | Totara Valley | 2024-08-12 11:10 | 45516.4653 | 2024-08-12 12:31 | 45516.5215 | 0.37726 | 0.0046575 | 158 | 12798 | Unplanned | Defective equipment | Broken pole #40354
654 |  | 3813 | G295 to End |  | Woodbury | 2024-08-12 11:23 | 45516.4743 | 2024-08-12 12:28 | 45516.5194 | 0.12071 | 0.0018571 | 63 | 4095 | Unplanned | Vegetation | Branches at Pole #11033
655 |  | 4719 | CB F107 (Totara Valley Rd) |  | Totara Valley | 2024-08-12 12:31 | 45516.5215 | 2024-08-12 17:36 | 45516.7333 | 0.56641 | 0.0018571 | 63 | 19215 | Unplanned | Defective equipment | Broken pole #40354
656 |  | 4719 | CB F107 (Totara Valley Rd) |  | Totara Valley | 2024-08-12 17:33 | 45516.7312 | 2024-08-12 17:36 | 45516.7333 | 0.0084011 | 0.0028004 | 95 | 285 | Unplanned | Defective equipment | Broken pole #40354
657 |  | 4719 | CB F150 (Langley Downs Rd) |  | Raincliff | 2024-08-12 17:33 | 45516.7312 | 2024-08-12 17:36 | 45516.7333 | 0.0068093 | 0.0022698 | 77 | 231 | Unplanned | Defective equipment | Broken pole #40354
658 |  | HTR054 | Links at pole #27513 |  | Mountainview | 2024-08-13 08:00 | 45517.3333 | 2024-08-13 11:55 | 45517.4965 | 0.048491 | 0.00020634 | 7 | 1645 | Planned | Planned interruption | Tree cutting
659 |  | RAK151A JMR691 | LB262 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 14:44 | 45517.6139 | 0.020163 | 5.8955e-05 | 2 | 684 | Planned | Planned interruption | PD Defect
660 |  | RAK151A JMR691 | E249-02 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:18 | 45517.6375 | 0.011084 | 2.9478e-05 | 1 | 376 | Planned | Planned interruption | PD Defect
661 |  | RAK151A JMR691 | E249-03 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:18 | 45517.6375 | 0.055418 | 0.00014739 | 5 | 1880 | Planned | Planned interruption | PD Defect
662 |  | RAK151A JMR691 | E249-06 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:18 | 45517.6375 | 0.088669 | 0.00023582 | 8 | 3008 | Planned | Planned interruption | PD Defect
663 |  | RAK151A JMR691 | DB1501 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:23 | 45517.641 | 0.033693 | 8.8433e-05 | 3 | 1143 | Planned | Planned interruption | PD Defect
664 |  | RAK151A JMR691 | DB1492 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:32 | 45517.6472 | 0.022993 | 5.8955e-05 | 2 | 780 | Planned | Planned interruption | PD Defect
665 |  | RAK151A JMR691 | DB1499 |  | Urban #2 | 2024-08-13 09:02 | 45517.3764 | 2024-08-13 15:26 | 45517.6431 | 0.022639 | 5.8955e-05 | 2 | 768 | Planned | Planned interruption | PD Defect
666 |  | SRS002 | ABS T499 (Rolleston Rd) |  | Rolleston Road | 2024-08-13 09:40 | 45517.4028 | 2024-08-13 11:58 | 45517.4986 | 0.0040679 | 2.9478e-05 | 1 | 138 | Unplanned | Defective equipment | Transformer repairs
667 |  | SRS002 | TX D1488 |  | Rolleston Road | 2024-08-13 09:40 | 45517.4028 | 2024-08-13 12:00 | 45517.5 | 0.0041269 | 2.9478e-05 | 1 | 140 | Unplanned | Defective equipment | Transformer repairs
668 |  | 00002 | LBS T541 |  | Orton | 2024-08-13 14:11 | 45517.591 | 2024-08-13 14:25 | 45517.6007 | 0.0012381 | 8.8433e-05 | 3 | 42 | Unplanned | Wildlife | Duck in TX DO Fuses
669 |  | HTR056 | ABS F168 - ABS F170 - ABS F169 |  | Cave | 2024-08-20 09:08 | 45524.3806 | 2024-08-20 15:36 | 45524.65 | 0.057187 | 0.00014739 | 5 | 1940 | Planned | Planned interruption | Tree cutting
670 |  | 3810 | CB W308 |  | Otaio | 2024-08-20 09:40 | 45524.4028 | 2024-08-20 10:53 | 45524.4535 | 0.025822 | 0.00035373 | 12 | 876 | Unplanned | Unknown | Broken Jumper
671 |  | JJV152 | ABS W345 |  | Otaio | 2024-08-21 08:00 | 45525.3333 | 2024-08-21 15:28 | 45525.6444 | 0.039618 | 8.8433e-05 | 3 | 1344 | Planned | Planned interruption | Transformer Upgrade
672 |  | JJV152 | 8 Murray St |  | Otaio | 2024-08-21 08:00 | 45525.3333 | 2024-08-21 15:42 | 45525.6542 | 0.013619 | 2.9478e-05 | 1 | 462 | Planned | Planned interruption | Transformer Upgrade
673 |  | 4720 | Fuses W127 |  | Morven | 2024-08-21 22:05 | 45525.9201 | 2024-08-22 00:03 | 45526.0021 | 0.052175 | 0.00044216 | 15 | 1770 | Unplanned | Unknown | Unknown
674 |  | 00003 | CB T626-ABS T675 |  | Rolleston Road | 2024-08-22 07:47 | 45526.3243 | 2024-08-22 08:56 | 45526.3722 | 0.36611 | 0.005306 | 180 | 12420 | Unplanned | Unknown | Unknown
675 |  | 00003 | ABS T675 |  | Rolleston Road | 2024-08-22 07:47 | 45526.3243 | 2024-08-22 09:14 | 45526.3847 | 0.012823 | 0.00014739 | 5 | 435 | Unplanned | Unknown | Unknown
676 |  | SKE1762 | RMU L489 |  | Old North Road | 2024-08-22 08:31 | 45526.3549 | 2024-08-22 16:38 | 45526.6931 | 0.014356 | 2.9478e-05 | 1 | 487 | Planned | Planned interruption | Transformer Maintenance
677 |  | CWL027 | TOA1539 |  | Morven | 2024-08-23 08:00 | 45527.3333 | 2024-08-23 10:05 | 45527.4201 | 0.0036847 | 2.9478e-05 | 1 | 125 | Planned | Planned interruption | Upgrade Disconnect
678 |  | HTR049 & SKE1787 | ABS T462 - D1403 '01' - D1402'01' |  | Mahan Road | 2024-08-23 09:00 | 45527.375 | 2024-08-23 13:56 | 45527.5806 | 0.20068 | 0.00067799 | 23 | 6808 | Planned | Planned interruption | Replace Red Tag Pole
679 |  | HTR049 & SKE1787 | D1403'01' |  | Mahan Road | 2024-08-23 09:00 | 45527.375 | 2024-08-23 14:13 | 45527.5924 | 0.0092265 | 2.9478e-05 | 1 | 313 | Planned | Planned interruption | Replace Red Tag Pole
680 |  | HTR049 & SKE1787 | D1402'01' |  | Mahan Road | 2024-08-23 09:00 | 45527.375 | 2024-08-23 14:05 | 45527.5868 | 0.026972 | 8.8433e-05 | 3 | 915 | Planned | Planned interruption | Replace Red Tag Pole
681 |  | SKE1761 | RMU L427 - RMU L481 |  | Old North Road | 2024-08-23 09:00 | 45527.375 | 2024-08-23 15:30 | 45527.6458 | 0.022993 | 5.8955e-05 | 2 | 780 | Planned | Planned interruption | Transformer Maintenance
682 |  | SRS003 | B871 LV OH - 7 Shaw St - 11 Shaw St - 14 Shaw St |  | Redruth 2 | 2024-08-25 08:09 | 45529.3396 | 2024-08-25 17:20 | 45529.7222 | 0.097453 | 0.00017687 | 6 | 3306 | Planned | Planned interruption | Tx B871 upgrade
683 |  | SRS003 | 7 Shaw St + 11 Shaw St + 14 Shaw St |  | Redruth 2 | 2024-08-25 08:09 | 45529.3396 | 2024-08-25 17:29 | 45529.7285 | 0.049522 | 8.8433e-05 | 3 | 1680 | Planned | Planned interruption | Tx B871 upgrade
684 |  | SRS003 | DB4038 |  | Redruth 2 | 2024-08-25 08:09 | 45529.3396 | 2024-08-25 17:45 | 45529.7396 | 0.050937 | 8.8433e-05 | 3 | 1728 | Planned | Planned interruption | Tx B871 upgrade
685 |  | SRS003 | DB4773 |  | Redruth 2 | 2024-08-25 08:09 | 45529.3396 | 2024-08-25 18:00 | 45529.75 | 0.034843 | 5.8955e-05 | 2 | 1182 | Planned | Planned interruption | Tx B871 upgrade
686 |  | SRS003 | Compactor Shed |  | Redruth 2 | 2024-08-25 08:09 | 45529.3396 | 2024-08-25 18:12 | 45529.7583 | 0.017775 | 2.9478e-05 | 1 | 603 | Planned | Planned interruption | Tx B871 upgrade
687 |  | SKE1782 | ABS T165 |  | Pleasant Point Township | 2024-08-26 08:15 | 45530.3438 | 2024-08-26 08:20 | 45530.3472 | 0.0030952 | 0.00061903 | 21 | 105 | Planned | Planned interruption | OH Refurbishment
688 |  | SKE1782 | CB L1159 - ABS T165 -B755'01' - B756'01' - B1133'01' - B1197'01' - D104'01' - B130'01' - B1503'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 16:53 | 45530.7035 | 0.39476 | 0.0007959 | 27 | 13392 | Planned | Planned interruption | OH Refurbishment
689 |  | SKE1782 | TX B755'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:09 | 45530.7146 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | OH Refurbishment
690 |  | SKE1782 | TX B756'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:18 | 45530.7208 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | OH Refurbishment
691 |  | SKE1782 | TX B1133'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:09 | 45530.7146 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | OH Refurbishment
692 |  | SKE1782 | TX B1197'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:12 | 45530.7167 | 0.030362 | 5.8955e-05 | 2 | 1030 | Planned | Planned interruption | OH Refurbishment
693 |  | SKE1782 | TX D104'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:32 | 45530.7306 | 0.031541 | 5.8955e-05 | 2 | 1070 | Planned | Planned interruption | OH Refurbishment
694 |  | SKE1782 | TX B1305'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:32 | 45530.7306 | 0.015771 | 2.9478e-05 | 1 | 535 | Planned | Planned interruption | OH Refurbishment
695 |  | SKE1782 | TX B1503'01' |  | Pleasant Point Township | 2024-08-26 08:37 | 45530.359 | 2024-08-26 17:21 | 45530.7229 | 0.030893 | 5.8955e-05 | 2 | 1048 | Planned | Planned interruption | OH Refurbishment
696 |  | 4721 | Fuses TOB749 |  | Hadlow | 2024-08-26 09:00 | 45530.375 | 2024-08-26 09:12 | 45530.3833 | 0.00035373 | 2.9478e-05 | 1 | 12 | Unplanned | Wildlife | Nest on HV Bushings
697 |  | SKE1783 &GWM1178 | TX B756'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 16:38 | 45531.6931 | 0.014356 | 2.9478e-05 | 1 | 487 | Planned | Planned interruption | OH Refurbishment
698 |  | SKE1783 &GWM1178 | TX B1197'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 16:49 | 45531.7007 | 0.02936 | 5.8955e-05 | 2 | 996 | Planned | Planned interruption | OH Refurbishment
699 |  | SKE1783 &GWM1178 | TX B1503'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 16:55 | 45531.7049 | 0.029713 | 5.8955e-05 | 2 | 1008 | Planned | Planned interruption | OH Refurbishment
700 |  | SKE1783 &GWM1178 | TX B1305'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 17:06 | 45531.7125 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | OH Refurbishment
701 |  | SKE1783 &GWM1178 | TX D104'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 17:18 | 45531.7208 | 0.031069 | 5.8955e-05 | 2 | 1054 | Planned | Planned interruption | OH Refurbishment
702 |  | SKE1783 &GWM1178 | CB L1159 - ABS T165 - B756'01' - B1197'01' - D104'01' - B130'01' - B1503'01' |  | Pleasant Point Township | 2024-08-27 08:31 | 45531.3549 | 2024-08-27 16:26 | 45531.6847 | 0.40605 | 0.00085485 | 29 | 13775 | Planned | Planned interruption | OH Refurbishment
703 |  | SKE1784 | ABS T165-205 Young Rd |  | Pleasant Point Township | 2024-08-28 08:58 | 45532.3736 | 2024-08-28 16:25 | 45532.684 | 0.26353 | 0.00058955 | 20 | 8940 | Planned | Planned interruption | Lines Maintenance
704 |  | SKE1784 | 205 Young Rd |  | Pleasant Point Township | 2024-08-28 08:58 | 45532.3736 | 2024-08-28 16:28 | 45532.6861 | 0.013265 | 2.9478e-05 | 1 | 450 | Planned | Planned interruption | Lines Maintenance
705 |  | HTR055 | Fuses F167 TO END |  | Cave | 2024-08-29 09:00 | 45533.375 | 2024-08-29 10:30 | 45533.4375 | 0.015918 | 0.00017687 | 6 | 540 | Planned | Planned interruption | Tree Trimming
706 |  | 00004 | ABS T224 |  | Temuka East | 2024-08-29 13:39 | 45533.5687 | 2024-08-29 16:47 | 45533.6993 | 1.8565 | 0.009875 | 335 | 62980 | Unplanned | Defective equipment | HV line broken
707 |  | 00004 | TMK CB8-ABS T224 |  | Temuka East | 2024-08-29 13:39 | 45533.5687 | 2024-08-29 15:30 | 45533.6458 | 3.6843 | 0.033192 | 1126 | 124986 | Unplanned | Defective equipment | HV line broken
708 |  | SKE1763 | ABS L456 ICP 1 |  | Waipopo | 2024-08-30 08:43 | 45534.3632 | 2024-08-30 14:31 | 45534.6049 | 0.010258 | 2.9478e-05 | 1 | 348 | Planned | Planned interruption | RMU & TX Maint
709 |  | SKE1763 | ABS L456 ICP 2 |  | Waipopo | 2024-08-30 08:43 | 45534.3632 | 2024-08-30 14:39 | 45534.6104 | 0.010494 | 2.9478e-05 | 1 | 356 | Planned | Planned interruption | RMU & TX Maint
710 |  | JRM030 | Fuses To A1424 |  | Otaio | 2024-08-30 09:14 | 45534.3847 | 2024-08-30 11:20 | 45534.4722 | 0.0037142 | 2.9478e-05 | 1 | 126 | Planned | Planned interruption | Transformer repairs
711 |  | WMR081 | Fuses F284 |  | Fairlie Rural | 2024-08-30 10:22 | 45534.4319 | 2024-08-30 11:02 | 45534.4597 | 0.0047164 | 0.00011791 | 4 | 160 | Unplanned | Defective equipment | Binder Repairs
712 |  | 3817 | ABY CB2742-ABS FX17 |  | Cave | 2024-09-01 15:35 | 45536.6493 | 2024-09-01 16:49 | 45536.7007 | 0.82673 | 0.011172 | 379 | 28046 | Unplanned | Adverse weather | Broken conductor due to wind
713 |  | 3817 | ABS FX17-CB F295 |  | Cave | 2024-09-01 15:35 | 45536.6493 | 2024-09-01 20:50 | 45536.8681 | 0.018571 | 5.8955e-05 | 2 | 630 | Unplanned | Adverse weather | Broken conductor due to wind
714 |  | 3817 | CB F295 |  | Cave | 2024-09-01 15:35 | 45536.6493 | 2024-09-01 17:12 | 45536.7167 | 0.094358 | 0.00097276 | 33 | 3201 | Unplanned | Adverse weather | Broken conductor due to wind
715 |  | 3814 | CB T565 to ABS T422 |  | Woodbury | 2024-09-01 18:36 | 45536.775 | 2024-09-02 08:31 | 45537.3549 | 1.1569 | 0.0013854 | 47 | 39245 | Unplanned | Adverse weather | High Winds
716 |  | 3814 | ABS T422 to ABS T426 |  | Woodbury | 2024-09-01 18:36 | 45536.775 | 2024-09-02 09:04 | 45537.3778 | 0.61408 | 0.00070746 | 24 | 20832 | Unplanned | Adverse weather | High Winds
717 |  | 3814 | ABS T426 to end |  | Woodbury | 2024-09-01 18:36 | 45536.775 | 2024-09-02 09:26 | 45537.3931 | 3.2007 | 0.0035963 | 122 | 108580 | Unplanned | Adverse weather | High Winds
718 |  | 3817 | CB L107 |  | Totara Valley | 2024-09-01 20:54 | 45536.8708 | 2024-09-01 20:56 | 45536.8722 | 0.0093149 | 0.0046575 | 158 | 316 | Unplanned | Adverse weather | Broken conductor due to wind
719 |  | 3817 | CB F295 |  | Cave | 2024-09-01 20:55 | 45536.8715 | 2024-09-01 21:06 | 45536.8792 | 0.0107 | 0.00097276 | 33 | 363 | Unplanned | Adverse weather | Broken conductor due to wind
720 |  | SKE1786 | Fuses D822 |  | Totara Valley | 2024-09-02 08:57 | 45537.3729 | 2024-09-02 15:42 | 45537.6542 | 0.023877 | 5.8955e-05 | 2 | 810 | Planned | Planned interruption | OH Refurbishment
721 |  | SKE1786 | ABS T165 - ABS T316 |  | Totara Valley | 2024-09-02 08:57 | 45537.3729 | 2024-09-02 15:21 | 45537.6396 | 0.21507 | 0.00056008 | 19 | 7296 | Planned | Planned interruption | OH Refurbishment
722 |  | 3815 | Fuses T489 to end |  | Woodbury | 2024-09-02 10:02 | 45537.4181 | 2024-09-02 12:12 | 45537.5083 | 0.030657 | 0.00023582 | 8 | 1040 | Unplanned | Adverse weather | High Winds
723 |  | 3812 | Fuses TO A115 |  | Otaio | 2024-09-02 10:46 | 45537.4486 | 2024-09-02 15:27 | 45537.6438 | 0.0082832 | 2.9478e-05 | 1 | 281 | Unplanned | Defective equipment | Broken Pole #40795
724 |  | 3819 | RGA 11- ABS T585 |  | Belfield | 2024-09-03 02:50 | 45538.1181 | 2024-09-03 04:07 | 45538.1715 | 0.21563 | 0.0028004 | 95 | 7315 | Unplanned | Adverse weather | Broken conductor due to wind
725 |  | 3819 | ABS T585-ABS T643 |  | Belfield | 2024-09-03 02:50 | 45538.1181 | 2024-09-03 04:48 | 45538.2 | 0.097394 | 0.00082537 | 28 | 3304 | Unplanned | Adverse weather | Broken conductor due to wind
726 |  | 3819 | ABS T643 |  | Belfield | 2024-09-03 02:50 | 45538.1181 | 2024-09-03 09:50 | 45538.4097 | 0.13619 | 0.00032425 | 11 | 4620 | Unplanned | Adverse weather | Broken conductor due to wind
727 |  | 3823 | CB T127-ABS TX20 |  | Rangitata | 2024-09-03 02:56 | 45538.1222 | 2024-09-03 04:11 | 45538.1743 | 0.015476 | 0.00020634 | 7 | 525 | Unplanned | Adverse weather | Broken pole - wind
728 |  | 3823 | ABS TX20-ABS TX62-Links T458 |  | Rangitata | 2024-09-03 02:56 | 45538.1222 | 2024-09-03 06:28 | 45538.2694 | 0.24997 | 0.0011791 | 40 | 8480 | Unplanned | Adverse weather | broken pole - wind
729 |  | 3823 | ABS TX62 |  | Rangitata | 2024-09-03 02:56 | 45538.1222 | 2024-09-03 04:30 | 45538.1875 | 0.024938 | 0.0002653 | 9 | 846 | Unplanned | Adverse weather | Broken pole wind
730 |  | 3823 | Links T458 |  | Rangitata | 2024-09-03 02:56 | 45538.1222 | 2024-09-03 05:08 | 45538.2139 | 0.070039 | 0.0005306 | 18 | 2376 | Unplanned | Adverse weather | Broken pole wind
731 |  | 3822 | Fuses L195 |  | Levels Plain | 2024-09-03 07:06 | 45538.2958 | 2024-09-03 14:54 | 45538.6208 | 0.068978 | 0.00014739 | 5 | 2340 | Unplanned | Adverse weather | Broken Pole & conductor due to wind
732 |  | 3820 | Fuses T488 |  | Rolleston Road | 2024-09-03 09:27 | 45538.3938 | 2024-09-03 10:52 | 45538.4528 | 0.29316 | 0.0034489 | 117 | 9945 | Unplanned | Adverse weather | Tree on lines and line repair due to wind
733 |  | 991 | Fuses L164 |  | Normanby | 2024-09-03 14:19 | 45538.5965 | 2024-09-03 14:28 | 45538.6028 | 0.0034489 | 0.00038321 | 13 | 117 | Unplanned | Adverse weather | Fencing wire on line
734 |  | 3821 | Links T421 |  | Woodbury | 2024-09-03 19:14 | 45538.8014 | 2024-09-03 20:38 | 45538.8597 | 0.039618 | 0.00047164 | 16 | 1344 | Unplanned | Adverse weather | Broken conductor due to wind
735 |  | SRT243 | B678-02 |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:30 | 45539.7292 | 0.14326 | 0.0002653 | 9 | 4860 | Planned | Planned interruption | Tim Maintenance
736 |  | SRT243 | ABS L601 |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:27 | 45539.7271 | 1.2347 | 0.0022993 | 78 | 41886 | Planned | Planned interruption | OH Refurbishment
737 |  | SRT243 | B696-06 FUSES |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:24 | 45539.7667 | 0.15759 | 0.0002653 | 9 | 5346 | Planned | Planned interruption | OH Refurbishment
738 |  | SRT243 | B696-05 FUSES |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:08 | 45539.7556 | 0.25557 | 0.00044216 | 15 | 8670 | Planned | Planned interruption | OH Refurbishment
739 |  | SRT243 | LB460 |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:12 | 45539.7583 | 0.034312 | 5.8955e-05 | 2 | 1164 | Planned | Planned interruption | OH Refurbishment
740 |  | SRT243 | B696-03 FUSES |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.13159 | 0.00023582 | 8 | 4464 | Planned | Planned interruption | OH Refurbishment
741 |  | SRT243 | B696-04 FUSES |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.39476 | 0.00070746 | 24 | 13392 | Planned | Planned interruption | OH Refurbishment
742 |  | SRT243 | 41 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment
743 |  | SRT243 | 39 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:51 | 45539.7438 | 0.016537 | 2.9478e-05 | 1 | 561 | Planned | Planned interruption | OH Refurbishment
744 |  | SRT243 | 42 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:58 | 45539.7486 | 0.016743 | 2.9478e-05 | 1 | 568 | Planned | Planned interruption | OH Refurbishment
745 |  | SRT243 | 46 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:01 | 45539.7507 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | OH Refurbishment
746 |  | SRT243 | 48 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:03 | 45539.7521 | 0.016891 | 2.9478e-05 | 1 | 573 | Planned | Planned interruption | OH Refurbishment
747 |  | SRT243 | 97 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:46 | 45539.7403 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | OH Refurbishment
748 |  | SRT243 | 95 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:49 | 45539.7424 | 0.016478 | 2.9478e-05 | 1 | 559 | Planned | Planned interruption | OH Refurbishment
749 |  | SRT243 | 94 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:45 | 45539.7396 | 0.01636 | 2.9478e-05 | 1 | 555 | Planned | Planned interruption | OH Refurbishment
750 |  | SRT243 | 93 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment
751 |  | SRT243 | 75 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment
752 |  | SRT243 | 77 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:52 | 45539.7444 | 0.016566 | 2.9478e-05 | 1 | 562 | Planned | Planned interruption | OH Refurbishment
753 |  | SRT243 | 81 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:45 | 45539.7396 | 0.01636 | 2.9478e-05 | 1 | 555 | Planned | Planned interruption | OH Refurbishment
754 |  | SRT243 | 84 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:46 | 45539.7403 | 0.01639 | 2.9478e-05 | 1 | 556 | Planned | Planned interruption | OH Refurbishment
755 |  | SRT243 | 86 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:49 | 45539.7424 | 0.016478 | 2.9478e-05 | 1 | 559 | Planned | Planned interruption | OH Refurbishment
756 |  | SRT243 | 88 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:50 | 45539.7431 | 0.016507 | 2.9478e-05 | 1 | 560 | Planned | Planned interruption | OH Refurbishment
757 |  | SRT243 | 83 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 18:01 | 45539.7507 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | OH Refurbishment
758 |  | SRT243 | 28 Luxmoore Rd |  | Grants Road | 2024-09-04 08:30 | 45539.3542 | 2024-09-04 17:48 | 45539.7417 | 0.016449 | 2.9478e-05 | 1 | 558 | Planned | Planned interruption | OH Refurbishment
759 |  | HTR057 | CB F295 |  | Cave | 2024-09-05 08:30 | 45540.3542 | 2024-09-05 08:33 | 45540.3562 | 0.0029183 | 0.00097276 | 33 | 99 | Planned | Planned interruption | Tree trimming
760 |  | SKE1834 | FUSES E315-02 |  | Lakeside Drive | 2024-09-05 09:00 | 45540.375 | 2024-09-05 14:42 | 45540.6125 | 0.030244 | 8.8433e-05 | 3 | 1026 | Planned | Planned interruption | RMU Maintenance
761 |  | HTR057 | ABS FX17 |  | Cave | 2024-09-05 09:00 | 45540.375 | 2024-09-05 14:58 | 45540.6236 | 0.021106 | 5.8955e-05 | 2 | 716 | Planned | Planned interruption | Tree trimming
762 |  | SRS008 | ABS W262 |  | Waihaorunga | 2024-09-09 08:48 | 45544.3667 | 2024-09-11 17:38 | 45546.7347 | 0.10052 | 2.9478e-05 | 1 | 3410 | Planned | Planned interruption | Installing NEW RMU
763 |  | SRT233 SRT234 | Fuses TOD13 |  | Temuka East | 2024-09-09 09:28 | 45544.3944 | 2024-09-09 14:58 | 45544.6236 | 0.35019 | 0.0010612 | 36 | 11880 | Planned | Planned interruption | Replace Drop out Fuses
764 |  | SRT233 SRT234 | 131 Richard Pearce Dr |  | Temuka East | 2024-09-09 09:28 | 45544.3944 | 2024-09-09 15:11 | 45544.6326 | 0.010111 | 2.9478e-05 | 1 | 343 | Planned | Planned interruption | Replace Drop out Fuses
765 |  | JDJ125 | Fusesn TO D789 |  | Waitohi | 2024-09-09 09:53 | 45544.4118 | 2024-09-09 12:44 | 45544.5306 | 0.010081 | 5.8955e-05 | 2 | 342 | Planned | Planned interruption | Transformer Replacement
766 |  | JDJ125 | Fusesn TO D789 |  | Waitohi | 2024-09-09 09:53 | 45544.4118 | 2024-09-09 12:36 | 45544.525 | 0.0048049 | 2.9478e-05 | 1 | 163 | Planned | Planned interruption | Transformer Replacement
767 |  | ACD165 | Fuses TOD857 |  | Belfield | 2024-09-10 09:00 | 45545.375 | 2024-09-10 13:50 | 45545.5764 | 0.0085485 | 2.9478e-05 | 1 | 290 | Planned | Planned interruption | Replace Pole
768 |  | HTR044 | Links F144 to end |  | Cave | 2024-09-10 09:00 | 45545.375 | 2024-09-10 13:55 | 45545.5799 | 0.2174 | 0.00073694 | 25 | 7375 | Planned | Planned interruption | Tree trimming
769 |  | SKE1758 | TE166-11 |  | June Street | 2024-09-10 09:00 | 45545.375 | 2024-09-10 09:12 | 45545.3833 | 0.0099045 | 0.00082537 | 28 | 336 | Planned | Planned interruption | RMU Maintenance
770 |  | SKE1758 | TE106-01 |  | June Street | 2024-09-10 09:00 | 45545.375 | 2024-09-10 09:21 | 45545.3896 | 0.050141 | 0.0023877 | 81 | 1701 | Planned | Planned interruption | RMU Maintenance
771 |  | SKE1758 | TE166-12 |  | June Street | 2024-09-10 09:00 | 45545.375 | 2024-09-10 09:10 | 45545.3819 | 0.0041269 | 0.00041269 | 14 | 140 | Planned | Planned interruption | RMU Maintenance
772 |  | SKE1758 | TE106-01 |  | June Street | 2024-09-10 15:30 | 45545.6458 | 2024-09-10 15:38 | 45545.6514 | 0.019102 | 0.0023877 | 81 | 648 | Planned | Planned interruption | RMU Maintenance
773 |  | SKE1758 | TE166-12 |  | June Street | 2024-09-10 15:54 | 45545.6625 | 2024-09-10 16:25 | 45545.684 | 0.012793 | 0.00041269 | 14 | 434 | Planned | Planned interruption | RMU Maintenance
774 |  | SKE1758 | TE166-11 |  | June Street | 2024-09-10 16:00 | 45545.6667 | 2024-09-10 16:10 | 45545.6736 | 0.007959 | 0.0007959 | 27 | 270 | Planned | Planned interruption | RMU Maintenance
775 |  | SKE1758 | 10a Brascombe Rd |  | June Street | 2024-09-10 16:00 | 45545.6667 | 2024-09-10 16:21 | 45545.6813 | 0.00061903 | 2.9478e-05 | 1 | 21 | Planned | Planned interruption | RMU Maintenance
776 |  | SKE1788 | Fuses TO TE53 |  | Le Cren Street | 2024-09-11 08:30 | 45546.3542 | 2024-09-11 18:55 | 45546.7882 | 0.90275 | 0.0014444 | 49 | 30625 | Planned | Planned interruption | R&T Cable
777 |  | 2850 | TE135-14 ,15, 16 |  | Le Cren Street | 2024-09-12 08:08 | 45547.3389 | 2024-09-12 08:13 | 45547.3424 | 0.0047164 | 0.00094328 | 32 | 160 | Unplanned | Human error | Incorrect Switch Operated
778 |  | 2849 | Beyond CB T127 Badham Road |  | Rangitata | 2024-09-12 08:52 | 45547.3694 | 2024-09-12 09:57 | 45547.4146 | 0.017244 | 0.0002653 | 9 | 585 | Unplanned | Unknown | Lines Down
779 |  | 2849 | Beyond CB T127 Badham Road |  | Rangitata | 2024-09-12 08:52 | 45547.3694 | 2024-09-12 10:03 | 45547.4187 | 0.037672 | 0.0005306 | 18 | 1278 | Unplanned | Unknown | Lines Down
780 |  | 2849 | Beyond CB T127 Badham Road |  | Rangitata | 2024-09-12 08:52 | 45547.3694 | 2024-09-12 11:05 | 45547.4618 | 0.027444 | 0.00020634 | 7 | 931 | Unplanned | Unknown | Lines Down
781 |  | 2849 | Beyond CB T127 Badham Road |  | Rangitata | 2024-09-12 08:52 | 45547.3694 | 2024-09-12 13:42 | 45547.5708 | 0.34194 | 0.0011791 | 40 | 11600 | Unplanned | Unknown | Lines Down
782 |  | 4724 | Fuses L862 |  | Levels Plain | 2024-09-13 09:59 | 45548.416 | 2024-09-13 10:21 | 45548.4313 | 0.0064851 | 0.00029478 | 10 | 220 | Unplanned | Defective equipment | Damaged Insulator
783 |  | 4723 | Links W745 |  | Tawai | 2024-09-13 12:03 | 45548.5021 | 2024-09-13 13:09 | 45548.5479 | 0.011673 | 0.00017687 | 6 | 396 | Unplanned | Vegetation | Trees over line
784 |  | 3818 | Fuses TOB460 |  | Cave | 2024-09-14 13:50 | 45549.5764 | 2024-09-14 16:40 | 45549.6944 | 0.015034 | 8.8433e-05 | 3 | 510 | Unplanned | Third party interference | LV lines broken by digger
785 |  | 3816 | CB W465 |  | Otaio | 2024-09-16 01:19 | 45551.0549 | 2024-09-16 05:56 | 45551.2472 | 0.68589 | 0.0024761 | 84 | 23268 | Unplanned | Wildlife | Possum on line
786 |  | 4725 | Fuses F252 |  | Fairlie Rural | 2024-09-17 06:50 | 45552.2847 | 2024-09-17 09:32 | 45552.3972 | 0.023877 | 0.00014739 | 5 | 810 | Planned | Planned interruption | Tree Branch on line
787 |  | 4726 | Links Z439 |  | Urban #2 | 2024-09-17 13:45 | 45552.5729 | 2024-09-17 14:58 | 45552.6236 | 0.13342 | 0.0018276 | 62 | 4526 | Unplanned | Defective equipment | Cracked insulators causing high PD Tx E130
788 |  | PJD1626 | ABY CB2742 minus LB ABS F402 |  | Cave | 2024-09-18 07:33 | 45553.3146 | 2024-09-18 09:35 | 45553.3993 | 0.21218 | 0.0017392 | 59 | 7198 | Planned | Planned interruption | ABY GXP Outage
789 |  | PJD1626 | ABY CB2722 (Fairlie) + ABY CB4242 |  | ABY-FLE 33kV | 2024-09-18 07:37 | 45553.3174 | 2024-09-18 09:35 | 45553.3993 | 0.010435 | 8.8433e-05 | 3 | 354 | Planned | Planned interruption | ABY GXP Outage
790 |  | PJD1626 | FLE CB F374 to end + ABS F212 to end |  | Cricklewood | 2024-09-18 07:37 | 45553.3174 | 2024-09-18 09:35 | 45553.3993 | 0.28175 | 0.0023877 | 81 | 9558 | Planned | Planned interruption | ABY GXP Outage
791 |  | PJD1626 | CB F380 (Fairlie Rural) to end |  | Fairlie Rural | 2024-09-18 07:37 | 45553.3174 | 2024-09-18 09:35 | 45553.3993 | 2.6853 | 0.022757 | 772 | 91096 | Planned | Planned interruption | ABY GXP Outage
792 |  | PJD1626 | FLE CB F383 (FLE TS) minus TX C269 Minus TX C308 |  | Fairlie Township | 2024-09-18 07:37 | 45553.3174 | 2024-09-18 09:35 | 45553.3993 | 0.99133 | 0.0084011 | 285 | 33630 | Planned | Planned interruption | ABY GXP Outage
793 |  | PJD1626 | TX C308 |  | Fairlie Township | 2024-09-18 07:37 | 45553.3174 | 2024-09-18 09:35 | 45553.3993 | 0.073046 | 0.00061903 | 21 | 2478 | Planned | Planned interruption | ABY GXP Outage
794 |  | PJD1626 | TX C308 minus LV Links at pole #15321 minus Gold Club |  | Fairlie Township | 2024-09-18 17:31 | 45553.7299 | 2024-09-18 17:45 | 45553.7396 | 0.0037142 | 0.0002653 | 9 | 126 | Planned | Planned interruption | ABY GXP Outage
795 |  | PJD1626 | Golf Club |  | Fairlie Township | 2024-09-18 17:31 | 45553.7299 | 2024-09-18 17:55 | 45553.7465 | 0.00070746 | 2.9478e-05 | 1 | 24 | Planned | Planned interruption | ABY GXP Outage
796 |  | PJD1626 | LV from Links at pole #15321 to end |  | Fairlie Township | 2024-09-18 17:31 | 45553.7299 | 2024-09-18 18:30 | 45553.7708 | 0.019131 | 0.00032425 | 11 | 649 | Planned | Planned interruption | ABY GXP Outage
797 |  | 5128 | TX Fuses TO A163 to end |  | Mt Studholme | 2024-09-18 17:34 | 45553.7319 | 2024-09-18 19:42 | 45553.8208 | 0.0075463 | 5.8955e-05 | 2 | 256 | Unplanned | Defective equipment | Broken Stay Wire
798 |  | PJD1626 | PLP CB2 (Sutherlands) to end |  | Cave | 2024-09-18 18:03 | 45553.7521 | 2024-09-18 18:04 | 45553.7528 | 0.0036847 | 0.0036847 | 125 | 125 | Unplanned | Defective equipment | LB ABS Flickers not engaged
799 |  | 5128 | Fuses W312 to end minus TX fuses TO A163 |  | Mt Studholme | 2024-09-18 19:10 | 45553.7986 | 2024-09-18 19:42 | 45553.8208 | 0.0028299 | 8.8433e-05 | 3 | 96 | Unplanned | Defective equipment | Broken Stay Wire
800 |  | 4727 | ABS T675 |  | Rolleston Road | 2024-09-18 23:50 | 45553.9931 | 2024-09-19 13:07 | 45554.5465 | 0.11747 | 0.00014739 | 5 | 3985 | Unplanned | Third party interference | Broken Pole and conductor
801 |  | 4727 | ABS T490 - ABS T675 |  | Rolleston Road | 2024-09-18 23:50 | 45553.9931 | 2024-09-19 01:58 | 45554.0819 | 0.53201 | 0.0041563 | 141 | 18048 | Unplanned | Third party interference | Broken Pole and conductor
802 |  | 4727 | CB T626-ABS T490 |  | Rolleston Road | 2024-09-18 23:50 | 45553.9931 | 2024-09-19 00:56 | 45554.0389 | 0.075875 | 0.0011496 | 39 | 2574 | Unplanned | Third party interference | Broken Pole and conductor
803 |  | 4730 | Links W742 |  | Morven | 2024-09-19 07:46 | 45554.3236 | 2024-09-19 10:10 | 45554.4236 | 0.055182 | 0.00038321 | 13 | 1872 | Unplanned | Defective equipment | Broken Conductor
804 |  | 994 | Fuses TOD214 |  | Rangitata | 2024-09-19 11:30 | 45554.4792 | 2024-09-19 11:38 | 45554.4847 | 0.00023582 | 2.9478e-05 | 1 | 8 | Unplanned | Wildlife | Bird's nest on Transformer
805 |  | 5127 | RGA CB13 to ABS T497 |  | Rangitata Island | 2024-09-21 09:56 | 45556.4139 | 2024-09-21 13:44 | 45556.5722 | 0.013442 | 5.8955e-05 | 2 | 456 | Unplanned | Third party interference | Car Vs Pole
806 |  | 5126 | Fusess L716 / ABS L717 to end |  | Hadlow | 2024-09-21 10:00 | 45556.4167 | 2024-09-21 12:35 | 45556.5243 | 0.68079 | 0.0043922 | 149 | 23095 | Unplanned | Unknown | Unkknown - Blown DO
807 |  | 5125 | Fuses G245 to end |  | Speechley | 2024-09-21 16:19 | 45556.6799 | 2024-09-21 17:47 | 45556.741 | 0.038911 | 0.00044216 | 15 | 1320 | Unplanned | Unknown | Unknown - Blown DO's
808 |  | 5023 | CB T626 (Rolleston Rd) - ABS T675 |  | Rolleston Road | 2024-09-21 18:43 | 45556.7799 | 2024-09-21 19:44 | 45556.8222 | 0.32366 | 0.005306 | 180 | 10980 | Unplanned | Defective equipment | Damaged Conductor between Pole #07206 and Pole #488723
809 |  | 5023 | ABS T675 |  | Rolleston Road | 2024-09-21 18:43 | 45556.7799 | 2024-09-21 22:22 | 45556.9319 | 0.032278 | 0.00014739 | 5 | 1095 | Unplanned | Defective equipment | Damaged Conductor between Pole #07206 and Pole #488723
810 |  | HTR062 | Fuses W161 |  | Morven | 2024-09-25 08:30 | 45560.3542 | 2024-09-25 13:57 | 45560.5813 | 0.067474 | 0.00020634 | 7 | 2289 | Planned | Planned interruption | Tree trimming
811 |  | HTR063A SRT263 | Links W134 - Links W601 - ABS W190 - Fuses W161 |  | Morven | 2024-09-25 08:30 | 45560.3542 | 2024-09-25 13:31 | 45560.5632 | 0.20407 | 0.00067799 | 23 | 6923 | Planned | Planned interruption | Tree trimming
812 |  | 4728 | ABS L171 - ABS L169 |  | Normanby | 2024-09-25 14:03 | 45560.5854 | 2024-09-25 15:47 | 45560.6576 | 0.088905 | 0.00085485 | 29 | 3016 | Unplanned | Defective equipment | Rotten Pole
813 |  | 4415 | TOD366 |  | Speechley | 2024-09-25 19:10 | 45560.7986 | 2024-09-25 20:33 | 45560.8562 | 0.0073399 | 8.8433e-05 | 3 | 249 | Unplanned | Unknown | Unknown -Bown Tx Fuses
814 |  | RAK141 | Links G292 |  | Speechley | 2024-09-26 08:36 | 45561.3583 | 2024-09-26 09:19 | 45561.3882 | 0.0012675 | 2.9478e-05 | 1 | 43 | Planned | Planned interruption | Installing NEW RMU
815 |  | JDJ116 JDJ117 | TOD426 |  | Temuka East | 2024-09-26 09:00 | 45561.375 | 2024-09-26 13:26 | 45561.5597 | 0.39205 | 0.0014739 | 50 | 13300 | Planned | Planned interruption | Replace Drop out Fuses
816 |  | JDJ116 JDJ117 | 9 Hyahurst St |  | Temuka East | 2024-09-26 09:00 | 45561.375 | 2024-09-26 13:41 | 45561.5701 | 0.0082832 | 2.9478e-05 | 1 | 281 | Planned | Planned interruption | Replace Drop out Fuses
817 |  | JDJ116 JDJ117 | 36 Hayhurst St |  | Temuka East | 2024-09-26 09:00 | 45561.375 | 2024-09-26 13:30 | 45561.5625 | 0.007959 | 2.9478e-05 | 1 | 270 | Planned | Planned interruption | Replace Drop out Fuses
818 |  | JDJ116 JDJ117 | 44 Hayhurst St |  | Temuka East | 2024-09-26 09:00 | 45561.375 | 2024-09-26 13:35 | 45561.566 | 0.0081064 | 2.9478e-05 | 1 | 275 | Planned | Planned interruption | Replace Drop out Fuses
819 |  | JDJ116 JDJ117 | 29 Denmark St |  | Temuka East | 2024-09-26 09:00 | 45561.375 | 2024-09-26 13:44 | 45561.5722 | 0.0083717 | 2.9478e-05 | 1 | 284 | Planned | Planned interruption | Replace Drop out Fuses
820 |  | JRM031 | Fuses TOB1996 |  | Cave | 2024-09-26 09:47 | 45561.4076 | 2024-09-26 12:10 | 45561.5069 | 0.0084306 | 5.8955e-05 | 2 | 286 | Planned | Planned interruption | LV earth bar rusting
821 |  | RAK141 | DB4759 |  | Speechley | 2024-09-26 17:31 | 45561.7299 | 2024-09-26 17:41 | 45561.7368 | 0.00029478 | 2.9478e-05 | 1 | 10 | Planned | Planned interruption | Installing NEW RMU
822 |  | 4601 | Fuses W155 |  | Waikakahi | 2024-10-02 11:47 | 45567.491 | 2024-10-02 12:19 | 45567.5132 | 0.006603 | 0.00020634 | 7 | 224 | Unplanned | Defective equipment | Remove wrap off crossarm pole #43887
823 |  | 4602 | ABS W309 to end |  | Otaio | 2024-10-02 14:49 | 45567.6174 | 2024-10-02 18:30 | 45567.7708 | 0.13029 | 0.00058955 | 20 | 4420 | Unplanned | Defective equipment | Red tagged Pole
824 |  | 4742 | Fuses TOC276 |  | Fairlie Rural | 2024-10-04 10:25 | 45569.434 | 2024-10-04 13:54 | 45569.5792 | 0.0061608 | 2.9478e-05 | 1 | 209 | Unplanned | Defective equipment | Defective Transformer
825 |  | 4416 | TO C44 to end |  | Cave | 2024-10-06 22:26 | 45571.9347 | 2024-10-07 15:35 | 45572.6493 | 0.060665 | 5.8955e-05 | 2 | 2058 | Unplanned | Defective equipment | Replace faulty Tx C44
826 |  | JDJ126 | TO D850 to end |  | Temuka West | 2024-10-07 09:00 | 45572.375 | 2024-10-07 11:00 | 45572.4583 | 0.13796 | 0.0011496 | 39 | 4680 | Planned | Planned interruption | Replace Drop out Fuses
827 |  | SRT264 | W510 to end |  | Ikawai | 2024-10-07 09:21 | 45572.3896 | 2024-10-07 10:13 | 45572.4257 | 0.013796 | 0.0002653 | 9 | 468 | Planned | Planned interruption | Replace red tag pole - outgae cancelled
828 |  | JDJ133 | TO C323 to end |  | Fairlie Rural | 2024-10-07 10:02 | 45572.4181 | 2024-10-07 15:42 | 45572.6542 | 0.010022 | 2.9478e-05 | 1 | 340 | Planned | Planned interruption | Replace Red Tag Pole
829 |  | SRS006 | TE61 cct 11 |  | Douglas Street | 2024-10-09 06:00 | 45574.25 | 2024-10-09 07:23 | 45574.3076 | 0.061166 | 0.00073694 | 25 | 2075 | Planned | Planned interruption | RMU replacement
830 |  | SRS006 | TE61 cct 12 |  | Douglas Street | 2024-10-09 06:00 | 45574.25 | 2024-10-09 07:23 | 45574.3076 | 0.0097866 | 0.00011791 | 4 | 332 | Planned | Planned interruption | RMU replacement
831 |  | SRS006 | TE61 cct 13 |  | Douglas Street | 2024-10-09 06:00 | 45574.25 | 2024-10-09 07:23 | 45574.3076 | 0.085633 | 0.0010317 | 35 | 2905 | Planned | Planned interruption | RMU replacement
832 |  | SRS006 | TE61 cct 14 |  | Douglas Street | 2024-10-09 06:00 | 45574.25 | 2024-10-09 07:20 | 45574.3056 | 0.037731 | 0.00047164 | 16 | 1280 | Planned | Planned interruption | RMU replacement
833 |  | SRS006 | TE61 cct 15 |  | Douglas Street | 2024-10-09 06:00 | 45574.25 | 2024-10-09 07:23 | 45574.3076 | 0.04404 | 0.0005306 | 18 | 1494 | Planned | Planned interruption | RMU replacement
834 |  | SRT265 & GWM1190 | W238 to end - A664 - A854 |  | Mt Studholme | 2024-10-09 08:32 | 45574.3556 | 2024-10-09 15:08 | 45574.6306 | 0.10506 | 0.0002653 | 9 | 3564 | Planned | Planned interruption | Tx upgrade and tree cutting
835 |  | SRT265 & GWM1190 | A664 |  | Mt Studholme | 2024-10-09 08:32 | 45574.3556 | 2024-10-09 15:14 | 45574.6347 | 0.01185 | 2.9478e-05 | 1 | 402 | Planned | Planned interruption | Tx upgrade and tree cutting
836 |  | SRT265 & GWM1190 | A854 |  | Mt Studholme | 2024-10-09 08:32 | 45574.3556 | 2024-10-09 15:29 | 45574.6451 | 0.012292 | 2.9478e-05 | 1 | 417 | Planned | Planned interruption | Tx upgrade and tree cutting
837 |  | SRS006 | TE61 cct 11 |  | Douglas Street | 2024-10-09 19:00 | 45574.7917 | 2024-10-09 20:19 | 45574.8465 | 0.058218 | 0.00073694 | 25 | 1975 | Planned | Planned interruption | RMU replacement
838 |  | SRS006 | TE61 cct 12 |  | Douglas Street | 2024-10-09 19:00 | 45574.7917 | 2024-10-09 20:29 | 45574.8535 | 0.010494 | 0.00011791 | 4 | 356 | Planned | Planned interruption | RMU replacement
839 |  | SRS006 | TE61 cct 13 |  | Douglas Street | 2024-10-09 19:00 | 45574.7917 | 2024-10-09 20:29 | 45574.8535 | 0.091823 | 0.0010317 | 35 | 3115 | Planned | Planned interruption | RMU replacement
840 |  | SRS006 | TE61 cct 14 |  | Douglas Street | 2024-10-09 19:00 | 45574.7917 | 2024-10-09 20:29 | 45574.8535 | 0.041976 | 0.00047164 | 16 | 1424 | Planned | Planned interruption | RMU replacement
841 |  | SRS006 | TE61 cct 15 |  | Douglas Street | 2024-10-09 19:00 | 45574.7917 | 2024-10-09 20:29 | 45574.8535 | 0.047223 | 0.0005306 | 18 | 1602 | Planned | Planned interruption | RMU replacement
842 |  | HTR066 | W190 - W279 |  | Morven | 2024-10-10 08:34 | 45575.3569 | 2024-10-10 09:44 | 45575.4056 | 0.012381 | 0.00017687 | 6 | 420 | Planned | Planned interruption | Tree cutting
843 |  | GWM1191 | TO B505 |  | Normanby | 2024-10-10 09:00 | 45575.375 | 2024-10-10 12:52 | 45575.5361 | 0.027355 | 0.00011791 | 4 | 928 | Planned | Planned interruption | Tree cutting
844 |  | JDJ134 | F218 |  | Fairlie Rural | 2024-10-10 10:00 | 45575.4167 | 2024-10-10 12:25 | 45575.5174 | 0.038468 | 0.0002653 | 9 | 1305 | Planned | Planned interruption | Replace red tagged pole
845 |  | 5141 | Fuses G185 |  | Woodbury | 2024-10-12 07:20 | 45577.3056 | 2024-10-12 09:18 | 45577.3875 | 0.031305 | 0.0002653 | 9 | 1062 | Unplanned | Unknown | Blown Fuses Cause Unknown
846 |  | 5142 | Fuses w132 |  | Glenavy | 2024-10-14 05:58 | 45579.2486 | 2024-10-14 06:22 | 45579.2653 | 0.0063672 | 0.0002653 | 9 | 216 | Unplanned | Wildlife | Blown Fuses Bird V Lines
847 |  | 4603 | Fuses TOB972 |  | Grants Road | 2024-10-14 08:00 | 45579.3333 | 2024-10-14 14:11 | 45579.591 | 0.42651 | 0.0011496 | 39 | 14469 | Unplanned | Third party interference | Truck vs pole #45941
848 |  | 4603 | Service Fuses from pole #45941/#488753 |  | Grants Road | 2024-10-14 08:00 | 45579.3333 | 2024-10-14 14:25 | 45579.6007 | 0.034047 | 8.8433e-05 | 3 | 1155 | Unplanned | Third party interference | Truck vs pole #45941
849 |  | SKE1795 | TX B1233 CCT4 to end (to DB2649) |  | Morgans Rd | 2024-10-15 08:30 | 45580.3542 | 2024-10-15 14:55 | 45580.6215 | 0.43126 | 0.0011202 | 38 | 14630 | Planned | Planned interruption | Sub Upgrade
850 |  | SKE1795 | TX B1233 CCT5 to end (to Hockey South Canterbury) |  | Morgans Rd | 2024-10-15 08:30 | 45580.3542 | 2024-10-15 15:02 | 45580.6264 | 0.011555 | 2.9478e-05 | 1 | 392 | Planned | Planned interruption | Sub Upgrade
851 |  | SKE1836 | ICP fed from LB161 |  | M158 | 2024-10-15 09:08 | 45580.3806 | 2024-10-15 14:37 | 45580.609 | 0.0096981 | 2.9478e-05 | 1 | 329 | Planned | Planned interruption | RMU & TX Maintenance
852 |  | SKE1836 | ICP's fed from DB1414 |  | M158 | 2024-10-15 09:08 | 45580.3806 | 2024-10-15 15:03 | 45580.6271 | 0.020929 | 5.8955e-05 | 2 | 710 | Planned | Planned interruption | RMU & TX Maintenance
853 |  | JRM033 | CB M357 to end |  | TEK-UHT 33kV | 2024-10-15 10:03 | 45580.4187 | 2024-10-15 14:28 | 45580.6028 | 0.0078116 | 2.9478e-05 | 1 | 265 | Planned | Planned interruption | CB Maintenance
854 |  | SKE1836 | ICP fed from LB161 |  | M158 | 2024-10-15 14:51 | 45580.6188 | 2024-10-15 14:54 | 45580.6208 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Planned | Planned interruption | RMU & TX Maintenance
855 |  | HTR047 | Links W131 to ABS WX19 |  | Glenavy | 2024-10-16 08:30 | 45581.3542 | 2024-10-16 12:37 | 45581.5257 | 0.36405 | 0.0014739 | 50 | 12350 | Planned | Planned interruption | Tree cutting
856 |  | SKE1901 | TX B992 to end |  | Morgans Rd | 2024-10-16 08:30 | 45581.3542 | 2024-10-16 16:42 | 45581.6958 | 0.10152 | 0.00020634 | 7 | 3444 | Planned | Planned interruption | Sub Upgrade
857 |  | SRT266 | Fuses L189 to end |  | Holme Station | 2024-10-16 09:00 | 45581.375 | 2024-10-16 14:50 | 45581.6181 | 0.041269 | 0.00011791 | 4 | 1400 | Planned | Planned interruption | TX Upgrade & O/H to U/G service conversion
858 |  | SKE1835 | DB1070 to end (UHT Lodge) |  | M158 | 2024-10-16 09:07 | 45581.3799 | 2024-10-16 14:18 | 45581.5958 | 0.0091676 | 2.9478e-05 | 1 | 311 | Planned | Planned interruption | RMU & TX Maintenance
859 |  | SKE1835 | TX E179 to end |  | M158 | 2024-10-16 09:07 | 45581.3799 | 2024-10-16 14:32 | 45581.6056 | 0.028741 | 8.8433e-05 | 3 | 975 | Planned | Planned interruption | RMU & TX Maintenance
860 |  | SKE1835 | TX E169 to end |  | M158 | 2024-10-16 09:07 | 45581.3799 | 2024-10-16 14:39 | 45581.6104 | 0.078293 | 0.00023582 | 8 | 2656 | Planned | Planned interruption | RMU & TX Maintenance
861 |  | SKE1835 | TX E168 to end |  | M158 | 2024-10-16 09:07 | 45581.3799 | 2024-10-16 14:45 | 45581.6146 | 0.0099634 | 2.9478e-05 | 1 | 338 | Planned | Planned interruption | RMU & TX Maintenance
862 |  | SRT267 | ABS M452 to end |  | Simons | 2024-10-17 10:00 | 45582.4167 | 2024-10-17 11:53 | 45582.4951 | 0.06995 | 0.00061903 | 21 | 2373 | Planned | Planned interruption | Replace connections
863 |  | LXL068 | TX E10 CCT 04 |  | Lakeside Drive | 2024-10-18 11:04 | 45583.4611 | 2024-10-18 14:26 | 45583.6014 | 0.071454 | 0.00035373 | 12 | 2424 | Planned | Planned interruption | TX E10 repairs
864 |  | LXL068 | TX E10 CCT 02 |  | Lakeside Drive | 2024-10-18 11:04 | 45583.4611 | 2024-10-18 14:26 | 45583.6014 | 0.16077 | 0.0007959 | 27 | 5454 | Planned | Planned interruption | TX E10 repairs
865 |  | LXL068 | TX E10 CCT 03 |  | Lakeside Drive | 2024-10-18 11:04 | 45583.4611 | 2024-10-18 14:26 | 45583.6014 | 0.11314 | 0.00056008 | 19 | 3838 | Planned | Planned interruption | TX E10 repairs
866 |  | LXL068 | TX E10 CCT 045 |  | Lakeside Drive | 2024-10-18 11:04 | 45583.4611 | 2024-10-18 14:26 | 45583.6014 | 0.059545 | 0.00029478 | 10 | 2020 | Planned | Planned interruption | TX E10 repairs
867 |  | LXL068 | TX E10 CCT 06 |  | Lakeside Drive | 2024-10-18 11:04 | 45583.4611 | 2024-10-18 14:26 | 45583.6014 | 0.11909 | 0.00058955 | 20 | 4040 | Planned | Planned interruption | TX E10 repairs
868 |  | SKE1691 | Trace from RMU L759 |  | Washdyke | 2024-10-19 08:17 | 45584.3451 | 2024-10-19 13:47 | 45584.5743 | 0.0097276 | 2.9478e-05 | 1 | 330 | Planned | Planned interruption | RMU & TX Maintenance
869 |  | HTR046 | ABS W121 |  | Glenavy | 2024-10-21 08:30 | 45586.3542 | 2024-10-21 15:47 | 45586.6576 | 0.48951 | 0.0011202 | 38 | 16606 | Planned | Planned interruption | Tree Cutting
870 |  | DVE371 | T420 - D301 - D1174 - D1877 |  | Woodbury | 2024-10-22 08:30 | 45587.3542 | 2024-10-22 16:33 | 45587.6896 | 0.32747 | 0.00067799 | 23 | 11109 | Planned | Planned interruption | Line Maintenance
871 |  | DVE371 | D301 |  | Woodbury | 2024-10-22 08:30 | 45587.3542 | 2024-10-22 16:42 | 45587.6958 | 0.029006 | 5.8955e-05 | 2 | 984 | Planned | Planned interruption | Line Maintenance
872 |  | DVE371 | D1174 |  | Woodbury | 2024-10-22 08:30 | 45587.3542 | 2024-10-22 17:03 | 45587.7104 | 0.030244 | 5.8955e-05 | 2 | 1026 | Planned | Planned interruption | Line Maintenance
873 |  | DVE371 | D1877 |  | Woodbury | 2024-10-22 08:30 | 45587.3542 | 2024-10-22 17:13 | 45587.7174 | 0.015417 | 2.9478e-05 | 1 | 523 | Planned | Planned interruption | Line Maintenance
874 |  | SKE1833 | E252 Cct 4 |  | Tekapo | 2024-10-22 09:04 | 45587.3778 | 2024-10-22 14:57 | 45587.6229 | 0.39541 | 0.0011202 | 38 | 13414 | Planned | Planned interruption | RMU & Tx Maintenance
875 |  | SKE1833 | M294 - E356-01 |  | Tekapo | 2024-10-22 09:15 | 45587.3854 | 2024-10-22 14:35 | 45587.6076 | 1.198 | 0.0037437 | 127 | 40640 | Planned | Planned interruption | RMU & Tx Maintenance
876 |  | SKE1833 | E356-01 |  | Tekapo | 2024-10-22 09:15 | 45587.3854 | 2024-10-22 14:50 | 45587.6181 | 0.45425 | 0.001356 | 46 | 15410 | Planned | Planned interruption | RMU & Tx Maintenance
877 |  | DVE372 | T420 |  | Woodbury | 2024-10-23 08:30 | 45588.3542 | 2024-10-23 16:59 | 45588.7076 | 0.42012 | 0.00082537 | 28 | 14252 | Planned | Planned interruption | Line Maintenance
878 |  | JRM041 | TX E366 CCT2 |  | Urban #2 | 2024-10-23 09:02 | 45588.3764 | 2024-10-23 13:02 | 45588.5431 | 0.0070746 | 2.9478e-05 | 1 | 240 | Planned | Planned interruption | Repair TX
879 |  | JRM041 | TX E366 CCT3 |  | Urban #2 | 2024-10-23 09:02 | 45588.3764 | 2024-10-23 13:11 | 45588.5493 | 0.02936 | 0.00011791 | 4 | 996 | Planned | Planned interruption | Repair TX
880 |  | JRM041 | TX E366 CCT5 |  | Urban #2 | 2024-10-23 09:02 | 45588.3764 | 2024-10-23 13:24 | 45588.5583 | 0.046339 | 0.00017687 | 6 | 1572 | Planned | Planned interruption | Repair TX
881 |  | DVE373 | Fuses T420 - Fuses T429 - TX D623 - TX D1687 - TX D673 - TX D1725 |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 16:56 | 45589.7056 | 0.13424 | 0.0002653 | 9 | 4554 | Planned | Planned interruption | Line Maintenance
882 |  | DVE373 | TX T429 to end |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 17:10 | 45589.7153 | 0.22993 | 0.00044216 | 15 | 7800 | Planned | Planned interruption | Line Maintenance
883 |  | DVE373 | TX D623 |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 17:18 | 45589.7208 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Line Maintenance
884 |  | DVE373 | TX D1687 |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 17:28 | 45589.7278 | 0.015859 | 2.9478e-05 | 1 | 538 | Planned | Planned interruption | Line Maintenance
885 |  | DVE373 | TX D673 |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 17:39 | 45589.7354 | 0.016183 | 2.9478e-05 | 1 | 549 | Planned | Planned interruption | Line Maintenance
886 |  | DVE373 | TX D1725 |  | Woodbury | 2024-10-24 08:30 | 45589.3542 | 2024-10-24 17:05 | 45589.7118 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | Line Maintenance
887 |  | GWM1194 | ABS T643 to end |  | Belfield | 2024-10-24 09:00 | 45589.375 | 2024-10-24 17:44 | 45589.7389 | 0.16991 | 0.00032425 | 11 | 5764 | Planned | Planned interruption | Tree cutting
888 |  | SRS017 | TX TE132-H341 CCT2- H339 CCT3 - LB B31 |  | Barnard Street | 2024-10-24 20:30 | 45589.8542 | 2024-10-25 04:04 | 45590.1694 | 0.25427 | 0.00056008 | 19 | 8626 | Planned | Planned interruption | Lucy Box H89 & B10 replacement
889 |  | SRS017 | LB B31- DB B30 |  | Barnard Street | 2024-10-24 20:30 | 45589.8542 | 2024-10-25 04:46 | 45590.1986 | 0.029242 | 5.8955e-05 | 2 | 992 | Planned | Planned interruption | Lucy Box H89 & B10 replacement
890 |  | SRS017 | DB B30 |  | Barnard Street | 2024-10-24 20:30 | 45589.8542 | 2024-10-25 05:01 | 45590.209 | 0.015063 | 2.9478e-05 | 1 | 511 | Planned | Planned interruption | Lucy Box H89 & B10 replacement
891 |  | 4604 | Fuses F108 to end |  | Cave | 2024-10-25 07:58 | 45590.3319 | 2024-10-25 10:55 | 45590.4549 | 0.010435 | 5.8955e-05 | 2 | 354 | Unplanned | Defective equipment | Broken Conductor
892 |  | SKE1909 | TX65 - T430 - Trace from Pole #08381 |  | Woodbury | 2024-10-25 10:24 | 45590.4333 | 2024-10-25 15:49 | 45590.659 | 0.15328 | 0.00047164 | 16 | 5200 | Planned | Planned interruption | Replace Pole and upgrade Transformer
893 |  | SKE1909 | TX D299 - 3ph ICP Fed From Pole #09434 |  | Woodbury | 2024-10-25 10:24 | 45590.4333 | 2024-10-25 16:01 | 45590.6674 | 0.039736 | 0.00011791 | 4 | 1348 | Planned | Planned interruption | Replace Pole and upgrade Transformer
894 |  | SKE1909 | 3ph ICP Fed From Pole #09434 |  | Woodbury | 2024-10-25 10:24 | 45590.4333 | 2024-10-25 16:10 | 45590.6736 | 0.010199 | 2.9478e-05 | 1 | 346 | Planned | Planned interruption | Replace Pole and upgrade Transformer
895 |  | 3825 | HLB CB M82- LBS M441 |  | Haldon-Lilybank 22kV | 2024-10-26 12:54 | 45591.5375 | 2024-10-26 13:44 | 45591.5722 | 0.02653 | 0.0005306 | 18 | 900 | Unplanned | Adverse weather | Broken Conductor - Snow
896 |  | 3825 | LBS M441 |  | Haldon-Lilybank 22kV | 2024-10-26 12:54 | 45591.5375 | 2024-10-26 16:58 | 45591.7069 | 0.27332 | 0.0011202 | 38 | 9272 | Unplanned | Adverse weather | Broken Conductor -Snow
897 |  | 4606 | Tx C341 |  | Fairlie Rural | 2024-10-26 19:15 | 45591.8021 | 2024-10-27 13:32 | 45592.5639 | 0.032337 | 2.9478e-05 | 1 | 1097 | Unplanned | Defective equipment | Broken Jumper at Pole #54293 / #54294
898 |  | 3824 | Fuses F222-ABS F403 |  | Fairlie Rural | 2024-10-27 11:18 | 45592.4708 | 2024-10-27 15:21 | 45592.6396 | 0.028652 | 0.00011791 | 4 | 972 | Unplanned | Adverse weather | Broken Conductor - weather
899 |  | 3824 | ABS F403 |  | Fairlie Rural | 2024-10-27 11:18 | 45592.4708 | 2024-10-27 15:29 | 45592.6451 | 0.014798 | 5.8955e-05 | 2 | 502 | Unplanned | Adverse weather | Broken Conductor weather
900 |  | 4606 | F226 - Tx C341 |  | Fairlie Rural | 2024-10-27 11:48 | 45592.4917 | 2024-10-27 13:32 | 45592.5639 | 0.030657 | 0.00029478 | 10 | 1040 | Unplanned | Defective equipment | Broken Jumper at Pole #54293 / #54294
901 |  | 4607 | PAR CB4 - W470 - L998 - B1018 |  | St Andrews | 2024-10-27 16:27 | 45592.6854 | 2024-10-27 17:45 | 45592.7396 | 0.37248 | 0.0047754 | 162 | 12636 | Unplanned | Defective equipment | Faulty Tx B1018
902 |  | 4607 | W470 |  | St Andrews | 2024-10-27 16:27 | 45592.6854 | 2024-10-27 18:05 | 45592.7535 | 0.52576 | 0.0053649 | 182 | 17836 | Unplanned | Defective equipment | Faulty Tx B1018
903 |  | 4607 | L998 |  | St Andrews | 2024-10-27 16:27 | 45592.6854 | 2024-10-27 18:12 | 45592.7583 | 0.23214 | 0.0022108 | 75 | 7875 | Unplanned | Defective equipment | Faulty Tx B1018
904 |  | 4607 | Tx B1018 |  | St Andrews | 2024-10-27 16:27 | 45592.6854 | 2024-10-30 13:45 | 45595.5729 | 0.24514 | 5.8955e-05 | 2 | 8316 | Unplanned | Defective equipment | Faulty Tx B1018
905 |  | 3826 | CB F359-ABS F248-ABS F313 |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 18:48 | 45593.7833 | 0.1078 | 0.0015623 | 53 | 3657 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
906 |  | 3826 | ABS F248 TO END |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 19:46 | 45593.8236 | 0.28452 | 0.0022403 | 76 | 9652 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
907 |  | 3826 | ABS F313-ABS F225-ABS F355 |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 19:12 | 45593.8 | 0.10692 | 0.0011496 | 39 | 3627 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
908 |  | 3826 | ABS F355 |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 19:41 | 45593.8201 | 0.10789 | 0.00088433 | 30 | 3660 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
909 |  | 3826 | ABS F225-Fuses F226 |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 20:29 | 45593.8535 | 0.19043 | 0.0011202 | 38 | 6460 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
910 |  | 3826 | Fuses F226 |  | Fairlie Rural | 2024-10-28 17:39 | 45593.7354 | 2024-10-28 21:27 | 45593.8938 | 0.07393 | 0.00032425 | 11 | 2508 | Unplanned | Third party interference | CB F359 Trip on EF - possible digger boom v lines
911 |  | DVE374 | Links T421 to end minus Links T744 - TX D620 - TX D1211 - TX D2120 - TX D307 |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:01 | 45594.6674 | 0.039883 | 8.8433e-05 | 3 | 1353 | Planned | Planned interruption | Line Maintenance
912 |  | DVE374 | Links T744 to end |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:32 | 45594.6889 | 0.085249 | 0.00017687 | 6 | 2892 | Planned | Planned interruption | Line Maintenance
913 |  | DVE374 | TX D620 to end |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:12 | 45594.675 | 0.013619 | 2.9478e-05 | 1 | 462 | Planned | Planned interruption | Line Maintenance
914 |  | DVE374 | TX D1211 to end |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:18 | 45594.6792 | 0.027591 | 5.8955e-05 | 2 | 936 | Planned | Planned interruption | Line Maintenance
915 |  | DVE374 | TX D2120 to end |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:22 | 45594.6819 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance
916 |  | DVE374 | TX D307 to end |  | Woodbury | 2024-10-29 08:30 | 45594.3542 | 2024-10-29 16:45 | 45594.6979 | 0.043774 | 8.8433e-05 | 3 | 1485 | Planned | Planned interruption | Line Maintenance
917 |  | HTR043A | Fuses W504 to end |  | Glenavy | 2024-10-29 08:54 | 45594.3708 | 2024-10-29 15:21 | 45594.6396 | 0.045631 | 0.00011791 | 4 | 1548 | Planned | Planned interruption | Tree cutting
918 |  | GWM1193 | ABS L221 to end |  | Totara Valley | 2024-10-29 09:00 | 45594.375 | 2024-10-29 13:55 | 45594.5799 | 0.46958 | 0.0015918 | 54 | 15930 | Planned | Planned interruption | Tree cutting
919 |  | SKE1898 | ABS T426 to end |  | Woodbury | 2024-10-29 10:05 | 45594.4201 | 2024-10-29 11:49 | 45594.4924 | 0.37401 | 0.0035963 | 122 | 12688 | Planned | Planned interruption | Connect WMG
920 |  | DVE375 | Fuses at pole #04780 to end |  | Woodbury | 2024-10-30 08:30 | 45595.3542 | 2024-10-30 12:17 | 45595.5118 | 0.0066914 | 2.9478e-05 | 1 | 227 | Planned | Planned interruption | Line Maintenance
921 |  | HTR043B | Fuses W504 to end |  | Glenavy | 2024-10-30 08:30 | 45595.3542 | 2024-10-30 15:07 | 45595.6299 | 0.046811 | 0.00011791 | 4 | 1588 | Planned | Planned interruption | Tree Cutting
922 |  | SKE1845 | RMU L528 minus RMU L581 minus #20 Chaucer St |  | Highfield | 2024-10-30 09:00 | 45595.375 | 2024-10-30 14:46 | 45595.6153 | 0.60176 | 0.0017392 | 59 | 20414 | Planned | Planned interruption | RMU & TX Maintenance
923 |  | SKE1845 | RMU L581 to end |  | Highfield | 2024-10-30 09:00 | 45595.375 | 2024-10-30 14:49 | 45595.6174 | 0.31892 | 0.00091381 | 31 | 10819 | Planned | Planned interruption | RMU & TX Maintenance
924 |  | SKE1845 | #20 Chaucer Street |  | Highfield | 2024-10-30 09:00 | 45595.375 | 2024-10-30 15:08 | 45595.6306 | 0.010848 | 2.9478e-05 | 1 | 368 | Planned | Planned interruption | RMU & TX Maintenance
925 |  | SRS010 | GRM CB5- TE50 CCT18-RMU E14-Links LB Q44 |  | Nile Street | 2024-10-30 09:00 | 45595.375 | 2024-10-30 09:24 | 45595.3917 | 0.1047 | 0.0043627 | 148 | 3552 | Planned | Planned interruption | DB Replacement
926 |  | SRS010 | TE50 CCT18-DB Q89-DB V12 |  | Nile Street | 2024-10-30 09:00 | 45595.375 | 2024-10-30 16:15 | 45595.6771 | 0.064114 | 0.00014739 | 5 | 2175 | Planned | Planned interruption | DB Replacement
927 |  | SRS010 | DB Q89 |  | Nile Street | 2024-10-30 09:00 | 45595.375 | 2024-10-30 16:23 | 45595.6826 | 0.065293 | 0.00014739 | 5 | 2215 | Planned | Planned interruption | DB Replacement
928 |  | SRS010 | DB V12 |  | Nile Street | 2024-10-30 09:00 | 45595.375 | 2024-10-30 16:50 | 45595.7014 | 0.096981 | 0.00020634 | 7 | 3290 | Planned | Planned interruption | DB Replacement
929 |  | SRS010 | GRM CB5- TE50 CCT18-RMU E14-Links LB Q44 |  | Nile Street | 2024-10-30 16:00 | 45595.6667 | 2024-10-30 16:15 | 45595.6771 | 0.06544 | 0.0043627 | 148 | 2220 | Planned | Planned interruption | DB Replacement
930 |  | SRS012 | CB T127 to ABS TX57 minus TX62 minus TX D911 |  | Rangitata | 2024-10-31 08:00 | 45596.3333 | 2024-10-31 15:26 | 45596.6431 | 0.60476 | 0.001356 | 46 | 20516 | Planned | Planned interruption | Yellow tagged pole
931 |  | SRS012 | TX D911 |  | Rangitata | 2024-10-31 08:00 | 45596.3333 | 2024-10-31 15:35 | 45596.6493 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Yellow tagged pole
932 |  | DVE377 | ABS T422 to Temp Links at pole #04506 minus TX D309 |  | Woodbury | 2024-10-31 09:12 | 45596.3833 | 2024-10-31 16:24 | 45596.6833 | 0.11461 | 0.0002653 | 9 | 3888 | Planned | Planned interruption | Line Maintenance
933 |  | DVE377 | TX D309 to end |  | Woodbury | 2024-10-31 09:12 | 45596.3833 | 2024-10-31 16:32 | 45596.6889 | 0.01297 | 2.9478e-05 | 1 | 440 | Planned | Planned interruption | Line Maintenance
934 |  | JRM035 | TX D1711 |  | Speechley | 2024-10-31 10:48 | 45596.45 | 2024-10-31 12:52 | 45596.5361 | 0.0036552 | 2.9478e-05 | 1 | 124 | Planned | Planned interruption | Remove ferro capacitor
935 |  | JRM035 | Fuses G272-TX D1711 |  | Speechley | 2024-10-31 10:48 | 45596.45 | 2024-10-31 12:38 | 45596.5264 | 0.0097276 | 8.8433e-05 | 3 | 330 | Planned | Planned interruption | Remove ferro capacitor
936 |  | DVE377 | Temp links at pole #04506 to Abs T426 minus TX D675 |  | Woodbury | 2024-10-31 17:30 | 45596.7292 | 2024-10-31 17:43 | 45596.7382 | 0.0049817 | 0.00038321 | 13 | 169 | Planned | Planned interruption | Line Maintenance
937 |  | DVE377 | TX D675 to end |  | Woodbury | 2024-10-31 17:30 | 45596.7292 | 2024-10-31 17:46 | 45596.7403 | 0.00047164 | 2.9478e-05 | 1 | 16 | Planned | Planned interruption | Line Maintenance
938 |  | DVE377 | ABS T426 to end |  | Woodbury | 2024-10-31 17:30 | 45596.7292 | 2024-10-31 17:49 | 45596.7424 | 0.068329 | 0.0035963 | 122 | 2318 | Planned | Planned interruption | Line Maintenance
939 |  | SRT264A | Fuses W510 to end |  | Waihao Downs | 2024-11-01 09:00 | 45597.375 | 2024-11-01 12:04 | 45597.5028 | 0.048815 | 0.0002653 | 9 | 1656 | Planned | Planned interruption | Red tagged Pole
940 |  | GWM1185 | Fuses L713 to end |  | Hadlow | 2024-11-02 09:00 | 45598.375 | 2024-11-02 13:45 | 45598.5729 | 0.11762 | 0.00041269 | 14 | 3990 | Planned | Planned interruption | Tree Cutting
941 |  | 3878 | Fuses T108 to end |  | Milford | 2024-11-02 18:02 | 45598.7514 | 2024-11-02 19:26 | 45598.8097 | 0.027237 | 0.00032425 | 11 | 924 | Unplanned | Adverse weather | Wind
942 |  | 3879 | RMU W699 MS to end |  | Waihaorunga | 2024-11-03 17:39 | 45599.7354 | 2024-11-03 17:55 | 45599.7465 | 0.0047164 | 0.00029478 | 10 | 160 | Unplanned | Vegetation | Branch removal
943 |  | SKE1757A | Tx E367 |  | Lakeside Drive | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:44 | 45600.6556 | 0.12793 | 0.00029478 | 10 | 4340 | Planned | Planned interruption | RMU maintenance & Tx upgrade
944 |  | SKE1757A | Tx E250 |  | Lakeside Drive | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:47 | 45600.6576 | 0.025763 | 5.8955e-05 | 2 | 874 | Planned | Planned interruption | RMU maintenance & Tx upgrade
945 |  | SKE1757A | Tx E311 |  | Lakeside Drive | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:50 | 45600.6597 | 0.02594 | 5.8955e-05 | 2 | 880 | Planned | Planned interruption | RMU maintenance & Tx upgrade
946 |  | SKE1757A | Tx E262 |  | Lakeside Drive | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:05 | 45600.6701 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | RMU maintenance & Tx upgrade
947 |  | SKE1757A | Tx E148 |  | Lakeside Drive | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:02 | 45600.6681 | 0.053296 | 0.00011791 | 4 | 1808 | Planned | Planned interruption | RMU maintenance & Tx upgrade
948 |  | SLA658 | from Temp Links pole #01505 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:52 | 45600.6611 | 0.11726 | 0.0002653 | 9 | 3978 | Planned | Planned interruption | Line Maintenance
949 |  | SLA658 | Tx D1816 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:24 | 45600.6833 | 0.013972 | 2.9478e-05 | 1 | 474 | Planned | Planned interruption | Line Maintenance
950 |  | SLA658 | Tx D323 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:28 | 45600.6861 | 0.028181 | 5.8955e-05 | 2 | 956 | Planned | Planned interruption | Line Maintenance
951 |  | SLA658 | Tx D324 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:22 | 45600.6819 | 0.013913 | 2.9478e-05 | 1 | 472 | Planned | Planned interruption | Line Maintenance
952 |  | SLA658 | Tx D1310 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:19 | 45600.6799 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Line Maintenance
953 |  | SLA658 | Tx D326 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 16:13 | 45600.6757 | 0.013648 | 2.9478e-05 | 1 | 463 | Planned | Planned interruption | Line Maintenance
954 |  | SLA657 | from temp links p#04932 - T423 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:32 | 45600.6472 | 0.22391 | 0.0005306 | 18 | 7596 | Planned | Planned interruption | Line Maintenance
955 |  | SLA657 | Tx D689 |  | Woodbury | 2024-11-04 08:30 | 45600.3542 | 2024-11-04 15:40 | 45600.6528 | 0.012675 | 2.9478e-05 | 1 | 430 | Planned | Planned interruption | Line Maintenance
956 |  | WMR116 | ABS W415 to end |  | Otaio | 2024-11-04 10:30 | 45600.4375 | 2024-11-04 10:59 | 45600.4576 | 0.0017097 | 5.8955e-05 | 2 | 58 | Planned | Planned interruption | Tap changes on Tx A1285 & A1299
957 |  | SLA657 | T423 |  | Woodbury | 2024-11-04 17:30 | 45600.7292 | 2024-11-04 17:43 | 45600.7382 | 0.055949 | 0.0043037 | 146 | 1898 | Planned | Planned interruption | Line Maintenance
958 |  | 4417 | G275 - G327 |  | Geraldine Township | 2024-11-04 19:28 | 45600.8111 | 2024-11-04 21:18 | 45600.8875 | 1.5175 | 0.013796 | 468 | 51480 | Unplanned | Unknown | Unknown - Possibly vegettion or bird strike
959 |  | 4417 | G327 |  | Geraldine Township | 2024-11-04 19:28 | 45600.8111 | 2024-11-04 21:26 | 45600.8931 | 0.43132 | 0.0036552 | 124 | 14632 | Unplanned | Unknown | Unknown - Possibly vegettion or bird strike
960 |  | 4608 | ABS L820 to end |  | Sutherland | 2024-11-06 14:01 | 45602.584 | 2024-11-06 17:13 | 45602.7174 | 0.056597 | 0.00029478 | 10 | 1920 | Unplanned | Defective equipment | Broken Jumper at ABS L820
961 |  | 4608 | ABS L1239 minus ABS L820 |  | Sutherland | 2024-11-06 16:02 | 45602.6681 | 2024-11-06 17:13 | 45602.7174 | 0.03558 | 0.00050112 | 17 | 1207 | Unplanned | Defective equipment | Broken Jumper at ABS L820
962 |  | DVE380 | from Temp Links pole #01505 |  | Woodbury | 2024-11-07 08:30 | 45603.3542 | 2024-11-07 15:38 | 45603.6514 | 0.1514 | 0.00035373 | 12 | 5136 | Planned | Planned interruption | Line Maintenance
963 |  | DVE380 | D1310 & individual ICPs |  | Woodbury | 2024-11-07 08:30 | 45603.3542 | 2024-11-07 15:45 | 45603.6562 | 0.038468 | 8.8433e-05 | 3 | 1305 | Planned | Planned interruption | Line Maintenance
964 |  | JRM040 | G242 minus D996-03 |  | Geraldine Township | 2024-11-08 10:39 | 45604.4437 | 2024-11-08 14:07 | 45604.5882 | 0.22073 | 0.0010612 | 36 | 7488 | Planned | Planned interruption | Tx Repairs
965 |  | WMR115 | TO Tx E230 |  | Pukaki | 2024-11-08 12:48 | 45604.5333 | 2024-11-08 12:53 | 45604.5368 | 0.00014739 | 2.9478e-05 | 1 | 5 | Planned | Planned interruption | Tap changes on Tx E230
966 |  | 4609 | TO D139 |  | Waitohi | 2024-11-09 11:08 | 45605.4639 | 2024-11-09 12:17 | 45605.5118 | 0.0081358 | 0.00011791 | 4 | 276 | Unplanned | Vegetation | Disconnect LV service line due to trees on line
967 |  | 4610 | G194 - G305 - G251 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 17:44 | 45605.7389 | 0.55103 | 0.005925 | 201 | 18693 | Unplanned | Vegetation | Trees on line P#08334
968 |  | 4610 | G251 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 17:46 | 45605.7403 | 0.40045 | 0.0042153 | 143 | 13585 | Unplanned | Vegetation | Trees on line P#08334
969 |  | 4610 | G253 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 21:40 | 45605.9028 | 0.10668 | 0.00032425 | 11 | 3619 | Unplanned | Defective equipment | Disc insulator broken P#08142
970 |  | 4610 | G178 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 19:25 | 45605.809 | 0.022875 | 0.00011791 | 4 | 776 | Unplanned | Vegetation | Trees on line P#08334
971 |  | 4610 | G136 - G137 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 19:25 | 45605.809 | 0.14869 | 0.00076642 | 26 | 5044 | Unplanned | Vegetation | Trees on line P#08334
972 |  | 4610 | G137 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 19:25 | 45605.809 | 0.074343 | 0.00038321 | 13 | 2522 | Unplanned | Vegetation | Trees on line P#08334
973 |  | 4610 | G305 - G136 - D178 - G253 |  | Speechley | 2024-11-09 16:11 | 45605.6743 | 2024-11-09 19:25 | 45605.809 | 0.22303 | 0.0011496 | 39 | 7566 | Unplanned | Vegetation | Trees on line P#08334
974 |  | 4610 | G178 |  | Speechley | 2024-11-09 19:27 | 45605.8104 | 2024-11-09 19:43 | 45605.8215 | 0.0018866 | 0.00011791 | 4 | 64 | Unplanned | Vegetation | Trees on line P#08334
975 |  | 4610 | G136 - G137 |  | Speechley | 2024-11-09 19:27 | 45605.8104 | 2024-11-09 19:34 | 45605.8153 | 0.0053649 | 0.00076642 | 26 | 182 | Unplanned | Vegetation | Trees on line P#08334
976 |  | 4610 | G137 |  | Speechley | 2024-11-09 19:27 | 45605.8104 | 2024-11-09 19:34 | 45605.8153 | 0.0026825 | 0.00038321 | 13 | 91 | Unplanned | Vegetation | Trees on line P#08334
977 |  | 4610 | G305 - G136 - D178 - G253 |  | Speechley | 2024-11-09 19:27 | 45605.8104 | 2024-11-09 19:34 | 45605.8153 | 0.0080474 | 0.0011496 | 39 | 273 | Unplanned | Vegetation | Trees on line P#08334
978 |  | 4610 | G136 - G137 |  | Speechley | 2024-11-09 19:35 | 45605.816 | 2024-11-09 19:56 | 45605.8306 | 0.016095 | 0.00076642 | 26 | 546 | Unplanned | Vegetation | Trees on line P#08334
979 |  | 4610 | G137 |  | Speechley | 2024-11-09 19:35 | 45605.816 | 2024-11-09 22:21 | 45605.9313 | 0.063613 | 0.00038321 | 13 | 2158 | Unplanned | Vegetation | Trees on line P#08334
980 |  | 4610 | G305 - G136 - D178 - G253 |  | Speechley | 2024-11-09 19:35 | 45605.816 | 2024-11-09 19:43 | 45605.8215 | 0.009197 | 0.0011496 | 39 | 312 | Unplanned | Vegetation | Trees on line P#08334
981 |  | JDJ127 | W308 TO END |  | Otaio | 2024-11-11 09:00 | 45607.375 | 2024-11-11 14:24 | 45607.6 | 0.11461 | 0.00035373 | 12 | 3888 | Planned | Planned interruption | Red tagged Pole
982 |  | 999 | Fuses L209 |  | Levels Plain | 2024-11-11 10:41 | 45607.4451 | 2024-11-11 12:38 | 45607.5264 | 0.3104 | 0.002653 | 90 | 10530 | Unplanned | Wildlife | Duck V pole
983 |  | 4743 | STU CB9 - Links W742 |  | Morven | 2024-11-11 14:17 | 45607.5951 | 2024-11-11 14:48 | 45607.6167 | 0.31252 | 0.010081 | 342 | 10602 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054
984 |  | 4743 | Links W742 - ABS W461 |  | Morven | 2024-11-11 14:17 | 45607.5951 | 2024-11-11 18:38 | 45607.7764 | 0.092324 | 0.00035373 | 12 | 3132 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054
985 |  | 4743 | ABS W461 |  | Morven | 2024-11-11 14:17 | 45607.5951 | 2024-11-11 18:42 | 45607.7792 | 0.0078116 | 2.9478e-05 | 1 | 265 | Unplanned | Defective equipment | Broke Conductor between Pole #32053 and Pole #32054
986 |  | DVE381 | TX D675 to end |  | Woodbury | 2024-11-12 08:30 | 45608.3542 | 2024-11-12 17:50 | 45608.7431 | 0.016507 | 2.9478e-05 | 1 | 560 | Planned | Planned interruption | Line Maintenance
987 |  | DVE381 | Tx D310 to end |  | Woodbury | 2024-11-12 08:30 | 45608.3542 | 2024-11-12 16:25 | 45608.684 | 0.028004 | 5.8955e-05 | 2 | 950 | Planned | Planned interruption | Line Maintenance
988 |  | DVE381 | Tx D1305 to end |  | Woodbury | 2024-11-12 08:30 | 45608.3542 | 2024-11-12 16:20 | 45608.6806 | 0.027709 | 5.8955e-05 | 2 | 940 | Planned | Planned interruption | Line Maintenance
989 |  | DVE381 | ABS T422 - Links at Pole #04506 - Tx D310 - Tx D675 - Tx D1305 |  | Woodbury | 2024-11-12 08:30 | 45608.3542 | 2024-11-12 16:03 | 45608.6687 | 0.08012 | 0.00017687 | 6 | 2718 | Planned | Planned interruption | Line Maintenance
990 |  | SKE1313 | Tx B1397 + Tx B899 + Tx B1078 |  | Highfield | 2024-11-12 09:49 | 45608.409 | 2024-11-12 17:34 | 45608.7319 | 3.1115 | 0.0066914 | 227 | 105555 | Planned | Planned interruption | Transformer maintenance
991 |  | 4612 | FUSES TO B1193 |  | Pleasant Point Township | 2024-11-12 16:08 | 45608.6722 | 2024-11-12 19:40 | 45608.8194 | 0.12499 | 0.00058955 | 20 | 4240 | Unplanned | Unknown | Fuses TOB1193 blown
992 |  | 4612 | FUSES TO B1193 |  | Pleasant Point Township | 2024-11-12 16:08 | 45608.6722 | 2024-11-12 19:53 | 45608.8285 | 0.14591 | 0.00064851 | 22 | 4950 | Unplanned | Unknown | Fuses TOB1193 blown
993 |  | 4612 | Fuses TO B1193 |  | Pleasant Point Township | 2024-11-12 16:08 | 45608.6722 | 2024-11-13 11:41 | 45609.4868 | 0.034577 | 2.9478e-05 | 1 | 1173 | Unplanned | Unknown | Fuses TOB1193 blown
994 |  | 4612 | Fuses TO B1193 |  | Pleasant Point Township | 2024-11-12 16:08 | 45608.6722 | 2024-11-13 08:00 | 45609.3333 | 0.028063 | 2.9478e-05 | 1 | 952 | Unplanned | Unknown | Fuses TOB1193 blown
995 |  | DVE381 | ABS T426 to end |  | Woodbury | 2024-11-12 17:41 | 45608.7368 | 2024-11-12 17:53 | 45608.7451 | 0.043155 | 0.0035963 | 122 | 1464 | Planned | Planned interruption | Line Maintenance
996 |  | DVE381 | Links at Pole #04506 - ABS T426 |  | Woodbury | 2024-11-12 17:41 | 45608.7368 | 2024-11-12 17:45 | 45608.7396 | 0.0016507 | 0.00041269 | 14 | 56 | Planned | Planned interruption | Line Maintenance
997 |  | SKE1889 | Tx E129-05 |  | M159 | 2024-11-13 08:30 | 45609.3542 | 2024-11-13 15:24 | 45609.6417 | 0.09763 | 0.00023582 | 8 | 3312 | Planned | Planned interruption | RMU replacement
998 |  | SKE1889 | LB74 |  | M159 | 2024-11-13 08:30 | 45609.3542 | 2024-11-13 15:27 | 45609.6438 | 0.049169 | 0.00011791 | 4 | 1668 | Planned | Planned interruption | RMU replacement
999 |  | DVE382 | ABS T422- ABS T426 - Tx D626 - Tx D675 |  | Woodbury | 2024-11-13 08:30 | 45609.3542 | 2024-11-13 16:10 | 45609.6736 | 0.29831 | 0.00064851 | 22 | 10120 | Planned | Planned interruption | Line Maintenance
1000 |  | DVE382 | Tx D626 |  | Woodbury | 2024-11-13 08:30 | 45609.3542 | 2024-11-13 16:25 | 45609.684 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Line Maintenance
1001 |  | DVE382 | TX D675 to end |  | Woodbury | 2024-11-13 08:30 | 45609.3542 | 2024-11-13 16:15 | 45609.6771 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Line Maintenance
1002 |  | GWM1195 | Fuses L226 to end |  | Sutherland | 2024-11-13 09:00 | 45609.375 | 2024-11-13 14:13 | 45609.5924 | 0.083039 | 0.0002653 | 9 | 2817 | Planned | Planned interruption | Tree Trimming
1003 |  | DVE382 | ABS T426 to end |  | Woodbury | 2024-11-13 17:38 | 45609.7347 | 2024-11-13 17:41 | 45609.7368 | 0.010789 | 0.0035963 | 122 | 366 | Planned | Planned interruption | Line Maintenance
1004 |  | 5024 | F284 to end |  | Fairlie Rural | 2024-11-14 04:50 | 45610.2014 | 2024-11-14 07:32 | 45610.3139 | 0.019102 | 0.00011791 | 4 | 648 | Unplanned | Unknown | Unknown
1005 |  | DVE383 | ABS T426 to end |  | Woodbury | 2024-11-14 07:45 | 45610.3229 | 2024-11-14 08:13 | 45610.3424 | 0.1007 | 0.0035963 | 122 | 3416 | Planned | Planned interruption | Line Maintenance
1006 |  | DVE383 | ABS T422 - ABS T426 |  | Woodbury | 2024-11-14 07:45 | 45610.3229 | 2024-11-14 08:20 | 45610.3472 | 0.024761 | 0.00070746 | 24 | 840 | Planned | Planned interruption | Line Maintenance
1007 |  | DVE383 | Links at Pole #04932 |  | Woodbury | 2024-11-14 07:45 | 45610.3229 | 2024-11-14 08:26 | 45610.3514 | 0.022963 | 0.00056008 | 19 | 779 | Planned | Planned interruption | Line Maintenance
1008 |  | SKE1890 | TX E154 |  | M159 | 2024-11-14 08:30 | 45610.3542 | 2024-11-14 10:17 | 45610.4285 | 0.012616 | 0.00011791 | 4 | 428 | Planned | Planned interruption | RMU replacement
1009 |  | SKE1890 | Tx E155 |  | M159 | 2024-11-14 08:30 | 45610.3542 | 2024-11-14 14:58 | 45610.6236 | 0.011437 | 2.9478e-05 | 1 | 388 | Planned | Planned interruption | RMU replacement
1010 |  | DVE383 | ABS TX48 - Links at Pole #04392 - Tx D1434 - Tx D1788 - Fuses T420 |  | Woodbury | 2024-11-14 08:31 | 45610.3549 | 2024-11-14 16:18 | 45610.6792 | 0.041298 | 8.8433e-05 | 3 | 1401 | Planned | Planned interruption | Line Maintenance
1011 |  | DVE383 | Tx D1434 to end |  | Woodbury | 2024-11-14 08:31 | 45610.3549 | 2024-11-14 16:37 | 45610.6924 | 0.014326 | 2.9478e-05 | 1 | 486 | Planned | Planned interruption | Line Maintenance
1012 |  | DVE383 | Tx D1788 to end |  | Woodbury | 2024-11-14 08:31 | 45610.3549 | 2024-11-14 16:34 | 45610.6903 | 0.014238 | 2.9478e-05 | 1 | 483 | Planned | Planned interruption | Line Maintenance
1013 |  | DVE383 | Fuses T420 to end |  | Woodbury | 2024-11-14 08:31 | 45610.3549 | 2024-11-14 16:25 | 45610.684 | 0.39123 | 0.00082537 | 28 | 13272 | Planned | Planned interruption | Line Maintenance
1014 |  | SKE1890 | TX E170 |  | M159 | 2024-11-14 08:37 | 45610.359 | 2024-11-14 10:12 | 45610.425 | 0.0028004 | 2.9478e-05 | 1 | 95 | Planned | Planned interruption | RMU replacement
1015 |  | 4744 | Fuses W460 |  | St Andrews | 2024-11-14 12:32 | 45610.5222 | 2024-11-14 15:15 | 45610.6354 | 0.024024 | 0.00014739 | 5 | 815 | Unplanned | Third party interference | Digger Vs OH lines pole #483854
1016 |  | DVE383 | Links at Pole #04932 |  | Woodbury | 2024-11-14 17:30 | 45610.7292 | 2024-11-14 17:46 | 45610.7403 | 0.077821 | 0.0048638 | 165 | 2640 | Planned | Planned interruption | Line Maintenance
1017 |  | SKE1899 | ABS T426 to end |  | Woodbury | 2024-11-15 09:20 | 45611.3889 | 2024-11-15 10:15 | 45611.4271 | 0.1978 | 0.0035963 | 122 | 6710 | Planned | Planned interruption | Disconnecting NWL Genset
1018 |  | LXL084 | Fuses TOD83 |  | Old Main South Road | 2024-11-15 15:14 | 45611.6347 | 2024-11-15 15:44 | 45611.6556 | 0.002653 | 8.8433e-05 | 3 | 90 | Unplanned | Lighting | Lightning at Tx D83
1019 |  | 5025 | Fuses TO D756 |  | Woodbury | 2024-11-15 18:20 | 45611.7639 | 2024-11-15 19:20 | 45611.8056 | 0.0088433 | 0.00014739 | 5 | 300 | Unplanned | Defective equipment | Jumper against X Arm at Pole #46013
1020 |  | SRS024 | Fuses TO B381 |  | Grants Road | 2024-11-18 09:00 | 45614.375 | 2024-11-18 10:41 | 45614.4451 | 0.17863 | 0.0017687 | 60 | 6060 | Planned | Planned interruption | Hotspot repair @ Tx B381
1021 |  | ACD168 | ABS W555 - TO A313 |  | Tawai | 2024-11-18 09:00 | 45614.375 | 2024-11-18 15:34 | 45614.6486 | 0.19744 | 0.00050112 | 17 | 6698 | Planned | Planned interruption | Replace P#33252 & upgrade Tx A313
1022 |  | ACD168 | TO A313 |  | Tawai | 2024-11-18 09:00 | 45614.375 | 2024-11-18 15:48 | 45614.6583 | 0.024054 | 5.8955e-05 | 2 | 816 | Planned | Planned interruption | Replace P#33252 & upgrade Tx A313
1023 |  | ACD169A | ABS L344 |  | Waitawa | 2024-11-18 09:06 | 45614.3792 | 2024-11-18 13:41 | 45614.5701 | 0.17834 | 0.00064851 | 22 | 6050 | Planned | Planned interruption | Upgrade Tx B2215
1024 |  | 4614 | M154 to M126 + E384 |  | M159 | 2024-11-18 15:49 | 45614.659 | 2024-11-18 17:09 | 45614.7146 | 0.075463 | 0.00094328 | 32 | 2560 | Unplanned | Defective equipment | Damaged Bushing on RMU
1025 |  | 4614 | M159 to M162 less E384 |  | M159 | 2024-11-18 15:49 | 45614.659 | 2024-11-18 17:35 | 45614.7326 | 0.015623 | 0.00014739 | 5 | 530 | Unplanned | Defective equipment | Damaged Bushing on RMU
1026 |  | 4614 | M125 |  | M159 | 2024-11-18 15:49 | 45614.659 | 2024-11-18 18:14 | 45614.7597 | 0.14105 | 0.00097276 | 33 | 4785 | Unplanned | Defective equipment | Damaged Bushing on RMU
1027 |  | 1201 | Fuses TOA313 |  | Tawai | 2024-11-19 07:37 | 45615.3174 | 2024-11-19 07:44 | 45615.3222 | 0.00020634 | 2.9478e-05 | 1 | 7 | Planned | Planned interruption | Tap change Tx A313
1028 |  | SRS025 | RMU M369 - ICP DB4715 |  | Lakeside Drive | 2024-11-19 09:00 | 45615.375 | 2024-11-19 10:10 | 45615.4236 | 0.13206 | 0.0018866 | 64 | 4480 | Planned | Planned interruption | Tx E183 Hotspot repairs
1029 |  | SRS025 | ICP DB4715 |  | Lakeside Drive | 2024-11-19 09:00 | 45615.375 | 2024-11-19 10:17 | 45615.4285 | 0.0022698 | 2.9478e-05 | 1 | 77 | Planned | Planned interruption | Tx E183 Hotspot repairs
1030 |  | DVE384 | ABS T419 - Tx D300 - Tx D751 - Tx D1278 - Tx D616 |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:30 | 45615.7292 | 3.0819 | 0.0060429 | 205 | 104550 | Planned | Planned interruption | Line Maintenance
1031 |  | DVE384 | Tx D300 |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:40 | 45615.7361 | 0.045985 | 8.8433e-05 | 3 | 1560 | Planned | Planned interruption | Line Maintenance
1032 |  | DVE384 | Tx D1278 |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:50 | 45615.7431 | 0.031246 | 5.8955e-05 | 2 | 1060 | Planned | Planned interruption | Line Maintenance
1033 |  | DVE384 | Tx D616 |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:41 | 45615.7368 | 0.015358 | 2.9478e-05 | 1 | 521 | Planned | Planned interruption | Line Maintenance
1034 |  | DVE384 | Tx D751 3pH ICP |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:46 | 45615.7403 | 0.015505 | 2.9478e-05 | 1 | 526 | Planned | Planned interruption | Line Maintenance
1035 |  | DVE384 | Tx D751 - Tx D751 3pH ICP |  | Woodbury | 2024-11-19 09:00 | 45615.375 | 2024-11-19 17:55 | 45615.7465 | 0.063082 | 0.00011791 | 4 | 2140 | Planned | Planned interruption | Line Maintenance
1036 |  | DVE384 | ABS T441 |  | Woodbury | 2024-11-19 09:03 | 45615.3771 | 2024-11-19 17:30 | 45615.7292 | 0.13451 | 0.0002653 | 9 | 4563 | Planned | Planned interruption | Line Maintenance
1037 |  | DVE384 | P#08381 - ABS T419 - ABS T441 |  | Woodbury | 2024-11-19 09:09 | 45615.3812 | 2024-11-19 17:28 | 45615.7278 | 0.058837 | 0.00011791 | 4 | 1996 | Planned | Planned interruption | Line Maintenance
1038 |  | SKE1892A | Tx E170 |  | M159 | 2024-11-20 08:00 | 45616.3333 | 2024-11-20 16:49 | 45616.7007 | 0.015594 | 2.9478e-05 | 1 | 529 | Planned | Planned interruption | Install & liven new RMU & Tx
1039 |  | DVE385 | Fuses T445 - Tx D1278 - Tx D1279 - Tx D300 |  | Woodbury | 2024-11-20 08:32 | 45616.3556 | 2024-11-20 15:47 | 45616.6576 | 0.038468 | 8.8433e-05 | 3 | 1305 | Planned | Planned interruption | Line Maintenance
1040 |  | DVE385 | Tx D1278 |  | Woodbury | 2024-11-20 08:32 | 45616.3556 | 2024-11-20 15:52 | 45616.6611 | 0.02594 | 5.8955e-05 | 2 | 880 | Planned | Planned interruption | Line Maintenance
1041 |  | DVE385 | Tx D1279 |  | Woodbury | 2024-11-20 08:32 | 45616.3556 | 2024-11-20 16:00 | 45616.6667 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Line Maintenance
1042 |  | DVE385 | Tx D300 |  | Woodbury | 2024-11-20 08:32 | 45616.3556 | 2024-11-20 16:08 | 45616.6722 | 0.040325 | 8.8433e-05 | 3 | 1368 | Planned | Planned interruption | Line Maintenance
1043 |  | SKE1893A | Tx E154-02 |  | M159 | 2024-11-21 08:00 | 45617.3333 | 2024-11-21 14:40 | 45617.6111 | 0.011791 | 2.9478e-05 | 1 | 400 | Planned | Planned interruption | Install new Tx E383
1044 |  | SKE1893A | Tx E154-03 |  | M159 | 2024-11-21 08:00 | 45617.3333 | 2024-11-21 14:50 | 45617.6181 | 0.012086 | 2.9478e-05 | 1 | 410 | Planned | Planned interruption | Install new Tx E383
1045 |  | SKE1893A | Tx E154-Metal workshop |  | M159 | 2024-11-21 08:00 | 45617.3333 | 2024-11-21 14:56 | 45617.6222 | 0.012263 | 2.9478e-05 | 1 | 416 | Planned | Planned interruption | Install new Tx E383
1046 |  | SKE1893A | Tx E154-Wood workshop |  | M159 | 2024-11-21 08:00 | 45617.3333 | 2024-11-21 15:16 | 45617.6361 | 0.012852 | 2.9478e-05 | 1 | 436 | Planned | Planned interruption | Install new Tx E383
1047 |  | DVE386 | Fuses T445 |  | Woodbury | 2024-11-21 08:30 | 45617.3542 | 2024-11-21 13:33 | 45617.5646 | 0.080386 | 0.0002653 | 9 | 2727 | Planned | Planned interruption | Line Maintenance
1048 |  | HTR072 | Fuses TO D608 |  | Woodbury | 2024-11-22 08:30 | 45618.3542 | 2024-11-22 10:43 | 45618.4465 | 0.015682 | 0.00011791 | 4 | 532 | Planned | Planned interruption | Tree cutting P#08373
1049 |  | DVE387 | ABS T441 - Tx D615 |  | Woodbury | 2024-11-22 08:30 | 45618.3542 | 2024-11-22 14:20 | 45618.5972 | 0.082537 | 0.00023582 | 8 | 2800 | Planned | Planned interruption | Line Maintenance
1050 |  | DVE387 | Tx D615 |  | Woodbury | 2024-11-22 08:30 | 45618.3542 | 2024-11-22 14:49 | 45618.6174 | 0.011172 | 2.9478e-05 | 1 | 379 | Planned | Planned interruption | Line Maintenance
1051 |  | ACD171 | Fuses W155 - Tx A1255 3pH ICP - Tx A1255 1pH ICP |  | Waikakahi | 2024-11-22 09:00 | 45618.375 | 2024-11-22 14:40 | 45618.6111 | 0.050112 | 0.00014739 | 5 | 1700 | Planned | Planned interruption | Pole replacement P#43887
1052 |  | ACD171 | Tx A1255 1pH ICP |  | Waikakahi | 2024-11-22 09:00 | 45618.375 | 2024-11-22 15:00 | 45618.625 | 0.010612 | 2.9478e-05 | 1 | 360 | Planned | Planned interruption | Pole replacement P#43887
1053 |  | ACD171 | Tx A1255 3pH ICP |  | Waikakahi | 2024-11-22 09:00 | 45618.375 | 2024-11-22 15:03 | 45618.6271 | 0.0107 | 2.9478e-05 | 1 | 363 | Planned | Planned interruption | Pole replacement P#43887
1054 |  | HTR074 | Fuses TO D255 |  | Speechley | 2024-11-22 13:00 | 45618.5417 | 2024-11-22 14:18 | 45618.5958 | 0.009197 | 0.00011791 | 4 | 312 | Planned | Planned interruption | Tree cutting P#03294 & P#03295
1055 |  | MCV633 | TX A817 to end |  | Morven | 2024-11-25 07:52 | 45621.3278 | 2024-11-25 08:07 | 45621.3382 | 0.00088433 | 5.8955e-05 | 2 | 30 | Planned | Planned interruption | Install Covers
1056 |  | HTR073 | Fuses F209 to end |  | Cricklewood | 2024-11-25 08:38 | 45621.3597 | 2024-11-25 10:43 | 45621.4465 | 0.051586 | 0.00041269 | 14 | 1750 | Planned | Planned interruption | Tree Cutting
1057 |  | ACD172 | Links F430 to end |  | Raincliff | 2024-11-25 09:01 | 45621.3757 | 2024-11-25 12:30 | 45621.5208 | 0.012322 | 5.8955e-05 | 2 | 418 | Planned | Planned interruption | Pole Repacement
1058 |  | DVE388 | ABS T426 to end minus #10 Horsfall Rd |  | Woodbury | 2024-11-26 08:30 | 45622.3542 | 2024-11-26 17:25 | 45622.7257 | 1.924 | 0.0035963 | 122 | 65270 | Planned | Planned interruption | Line Maintenance
1059 |  | DVE388 | TX D627 to end |  | Woodbury | 2024-11-26 08:30 | 45622.3542 | 2024-11-26 17:33 | 45622.7312 | 0.016006 | 2.9478e-05 | 1 | 543 | Planned | Planned interruption | Line Maintenance
1060 |  | DVE388 | Temp Links to ABS T426 minus TX D627 minus TX D675 |  | Woodbury | 2024-11-26 08:32 | 45622.3556 | 2024-11-26 17:10 | 45622.7153 | 0.16796 | 0.00032425 | 11 | 5698 | Planned | Planned interruption | Line Maintenance
1061 |  | DVE388 | #10 Horsefall Rd |  | Woodbury | 2024-11-26 08:32 | 45622.3556 | 2024-11-26 17:38 | 45622.7347 | 0.016095 | 2.9478e-05 | 1 | 546 | Planned | Planned interruption | Line Maintenance
1062 |  | DVE388 | TX D675 to end |  | Woodbury | 2024-11-26 08:32 | 45622.3556 | 2024-11-26 17:20 | 45622.7222 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Line Maintenance
1063 |  | SKE1896 | TX E153 /2 to end minus #1 De Faur Place |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:17 | 45623.5951 | 0.051144 | 0.00014739 | 5 | 1735 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1064 |  | SKE1896 | #1 De Faur Place |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:53 | 45623.6201 | 0.01129 | 2.9478e-05 | 1 | 383 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1065 |  | SKE1896 | TX E153 /3 to end |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:36 | 45623.6083 | 0.17262 | 0.00047164 | 16 | 5856 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1066 |  | SKE1896 | TX E153 /4 to end minus 3/7 Wakefield Drive |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:28 | 45623.6028 | 0.094977 | 0.0002653 | 9 | 3222 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1067 |  | SKE1896 | 3/7 Wakefiled Drive |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:52 | 45623.6194 | 0.01126 | 2.9478e-05 | 1 | 382 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1068 |  | SKE1896 | TX E153/5 to end (DB1210 / #4 Kitchener Dr) |  | M159 | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 14:50 | 45623.6181 | 0.011202 | 2.9478e-05 | 1 | 380 | Planned | Planned interruption | Mt Cook RMU & TX's Upgrade
1069 |  | DVE389 | Temp links at pole #04383 to End minus TX D675, D1767 and TX D320 ICP #1 & ICP #2 |  | Woodbury | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 16:20 | 45623.6806 | 0.083127 | 0.00017687 | 6 | 2820 | Planned | Planned interruption | Line Maintenance
1070 |  | DVE389 | TX D675 to end |  | Woodbury | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 16:29 | 45623.6868 | 0.01412 | 2.9478e-05 | 1 | 479 | Planned | Planned interruption | Line Maintenance
1071 |  | DVE389 | TX D1767 to end |  | Woodbury | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 16:44 | 45623.6972 | 0.014562 | 2.9478e-05 | 1 | 494 | Planned | Planned interruption | Line Maintenance
1072 |  | DVE389 | TX D320 ICP #1 |  | Woodbury | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 16:49 | 45623.7007 | 0.014709 | 2.9478e-05 | 1 | 499 | Planned | Planned interruption | Line Maintenance
1073 |  | DVE389 | TX D320 ICP #2 |  | Woodbury | 2024-11-27 08:30 | 45623.3542 | 2024-11-27 17:02 | 45623.7097 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | Line Maintenance
1074 |  | DVE394 | Fuses T424 to end minus TX D320, D311 , D321 |  | Woodbury | 2024-11-28 08:30 | 45624.3542 | 2024-11-28 15:19 | 45624.6382 | 0.072338 | 0.00017687 | 6 | 2454 | Planned | Planned interruption | Line Maintenance
1075 |  | DVE394 | TX D320 |  | Woodbury | 2024-11-28 08:30 | 45624.3542 | 2024-11-28 15:36 | 45624.65 | 0.025115 | 5.8955e-05 | 2 | 852 | Planned | Planned interruption | Line Maintenance
1076 |  | DVE394 | TX D311 |  | Woodbury | 2024-11-28 08:30 | 45624.3542 | 2024-11-28 15:44 | 45624.6556 | 0.012793 | 2.9478e-05 | 1 | 434 | Planned | Planned interruption | Line Maintenance
1077 |  | DVE394 | TX D321 |  | Woodbury | 2024-11-28 08:30 | 45624.3542 | 2024-11-28 15:58 | 45624.6653 | 0.013206 | 2.9478e-05 | 1 | 448 | Planned | Planned interruption | Line Maintenance
1078 |  | JRM046 | TX E248 Sewer Pump |  | Lakeside Drive | 2024-11-28 10:18 | 45624.4292 | 2024-11-28 13:53 | 45624.5785 | 0.0063377 | 2.9478e-05 | 1 | 215 | Planned | Planned interruption | TX Maintenance
1079 |  | JRM046 | TX E248 Toilet Block |  | Lakeside Drive | 2024-11-28 10:18 | 45624.4292 | 2024-11-28 13:43 | 45624.5715 | 0.0060429 | 2.9478e-05 | 1 | 205 | Planned | Planned interruption | TX Maintenance
1080 |  | 4619 | Recloser F418 |  | Raincliff | 2024-11-28 21:18 | 45624.8875 | 2024-11-29 01:16 | 45625.0528 | 0.30167 | 0.0012675 | 43 | 10234 | Unplanned | Vegetation | Tree Branch on line at pole #48318
1081 |  | 4615 | TVS CB Z3 to end |  | Pukaki | 2024-11-29 13:51 | 45625.5771 | 2024-11-29 14:45 | 45625.6146 | 0.070039 | 0.001297 | 44 | 2376 | Unplanned | Wildlife | Possum on lines
1082 |  | 4620 | Fuses F129 |  | Totara Valley | 2024-11-30 06:10 | 45626.2569 | 2024-11-30 06:55 | 45626.2882 | 0.007959 | 0.00017687 | 6 | 270 | Unplanned | Third party interference | Possible water from irrigator
1083 |  | SRT278 | From Pole #09232 - 2 ICP fed from Pole 09238 |  | Winchester | 2024-12-02 08:37 | 45628.359 | 2024-12-02 16:39 | 45628.6937 | 0.085249 | 0.00017687 | 6 | 2892 | Planned | Planned interruption | Line Maintenance
1084 |  | SRT278 | 2 ICP fed from Pole 09238 |  | Winchester | 2024-12-02 08:37 | 45628.359 | 2024-12-02 16:51 | 45628.7021 | 0.029124 | 5.8955e-05 | 2 | 988 | Planned | Planned interruption | Line Maintenance
1085 |  | HTR082 | Links W740 |  | Waihuna | 2024-12-02 08:54 | 45628.3708 | 2024-12-02 14:36 | 45628.6083 | 0.07057 | 0.00020634 | 7 | 2394 | Planned | Planned interruption | Tree Cutting
1086 |  | 4616 | Fuses W526 to end |  | Waikakahi | 2024-12-02 10:37 | 45628.4424 | 2024-12-02 14:16 | 45628.5944 | 0.15493 | 0.00070746 | 24 | 5256 | Unplanned | Third party interference | Tree fell on lines
1087 |  | 4617 | ABS T579 to end |  | Milford | 2024-12-02 16:49 | 45628.7007 | 2024-12-02 17:01 | 45628.709 | 0.00070746 | 5.8955e-05 | 2 | 24 | Unplanned | Defective equipment | TMK CB2 Overload
1088 |  | 4617 | Links T121 minus ABS T579 |  | Milford | 2024-12-02 16:53 | 45628.7035 | 2024-12-02 16:58 | 45628.7069 | 0.0022108 | 0.00044216 | 15 | 75 | Unplanned | Defective equipment | TMK CB2 Overload
1089 |  | 4618 | Fuses G236 to end |  | Speechley | 2024-12-03 05:58 | 45629.2486 | 2024-12-03 09:02 | 45629.3764 | 0.016272 | 8.8433e-05 | 3 | 552 | Unplanned | Defective equipment | Line on ground - Corroded / Rotten termination at Dead end
1090 |  | DVE391 | From Temp Links at Pole #01505 - D323 - D1816 - D324 - D1310 - D326 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 15:56 | 45629.6639 | 0.11487 | 0.0002653 | 9 | 3897 | Planned | Planned interruption | Line Maintenance
1091 |  | DVE391 | From D323 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 16:00 | 45629.6667 | 0.025763 | 5.8955e-05 | 2 | 874 | Planned | Planned interruption | Line Maintenance
1092 |  | DVE391 | From D1816 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 16:02 | 45629.6681 | 0.012941 | 2.9478e-05 | 1 | 439 | Planned | Planned interruption | Line Maintenance
1093 |  | DVE391 | From D324 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 16:08 | 45629.6722 | 0.013118 | 2.9478e-05 | 1 | 445 | Planned | Planned interruption | Line Maintenance
1094 |  | DVE391 | From D1310 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 16:14 | 45629.6764 | 0.013294 | 2.9478e-05 | 1 | 451 | Planned | Planned interruption | Line Maintenance
1095 |  | DVE391 | From D326 |  | Woodbury | 2024-12-03 08:43 | 45629.3632 | 2024-12-03 16:19 | 45629.6799 | 0.013442 | 2.9478e-05 | 1 | 456 | Planned | Planned interruption | Line Maintenance
1096 |  | HTR083 | From ABS W158 |  | Waikakahi | 2024-12-04 07:37 | 45630.3174 | 2024-12-04 07:38 | 45630.3181 | 0.00070746 | 0.00070746 | 24 | 24 | Planned | Planned interruption | Tree Cutting
1097 |  | HTR083 | From ABS WX46 - W158 - WX45 |  | Waikakahi | 2024-12-04 08:00 | 45630.3333 | 2024-12-04 16:06 | 45630.6708 | 0.12894 | 0.0002653 | 9 | 4374 | Planned | Planned interruption | Tree Cutting
1098 |  | DVE392 | From Temp Links at Pole #01505 - D323 - D1816 - D324 - D1310 - D326 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:40 | 45630.6528 | 0.11408 | 0.0002653 | 9 | 3870 | Planned | Planned interruption | Line Maintenance
1099 |  | DVE392 | From D323 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:46 | 45630.6569 | 0.025705 | 5.8955e-05 | 2 | 872 | Planned | Planned interruption | Line Maintenance
1100 |  | DVE392 | From D1816 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:45 | 45630.6562 | 0.012823 | 2.9478e-05 | 1 | 435 | Planned | Planned interruption | Line Maintenance
1101 |  | DVE392 | From D324 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:49 | 45630.659 | 0.012941 | 2.9478e-05 | 1 | 439 | Planned | Planned interruption | Line Maintenance
1102 |  | DVE392 | From D1310 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:56 | 45630.6639 | 0.013147 | 2.9478e-05 | 1 | 446 | Planned | Planned interruption | Line Maintenance
1103 |  | DVE392 | From D326 |  | Woodbury | 2024-12-04 08:30 | 45630.3542 | 2024-12-04 15:47 | 45630.6576 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Line Maintenance
1104 |  | HTR083 | From ABS W158 |  | Waikakahi | 2024-12-04 17:25 | 45630.7257 | 2024-12-04 17:26 | 45630.7264 | 0.00070746 | 0.00070746 | 24 | 24 | Planned | Planned interruption | Tree Cutting
1105 |  | DVE393 | From T429 - D1301 |  | Woodbury | 2024-12-05 08:30 | 45631.3542 | 2024-12-05 14:56 | 45631.6222 | 0.1593 | 0.00041269 | 14 | 5404 | Planned | Planned interruption | Line Maintenance
1106 |  | DVE393 | From D1301 |  | Woodbury | 2024-12-05 08:30 | 45631.3542 | 2024-12-05 15:03 | 45631.6271 | 0.011585 | 2.9478e-05 | 1 | 393 | Planned | Planned interruption | Line Maintenance
1107 |  | 4621 | From RMU Z105 |  | Glen Lyon | 2024-12-05 09:00 | 45631.375 | 2024-12-05 10:30 | 45631.4375 | 0.034489 | 0.00038321 | 13 | 1170 | Unplanned | Defective equipment | Line Repair
1108 |  | HTR085 | TOA317 Fuses |  | Tawai | 2024-12-06 08:00 | 45632.3333 | 2024-12-06 13:05 | 45632.5451 | 0.0089907 | 2.9478e-05 | 1 | 305 | Planned | Planned interruption | Tree trimming
1109 |  | JRM049 | RMU L381 to RMU L973 |  | Arowhenua | 2024-12-08 08:33 | 45634.3562 | 2024-12-08 14:46 | 45634.6153 | 0.010995 | 2.9478e-05 | 1 | 373 | Planned | Planned interruption | RMU replacement
1110 |  | 5144 | CB T565 |  | Woodbury | 2024-12-08 12:37 | 45634.5257 | 2024-12-08 13:07 | 45634.5465 | 0.17068 | 0.0056892 | 193 | 5790 | Unplanned | Unknown | Lines down
1111 |  | 1301 | CB G249-LB ABS G353 |  | Woodbury | 2024-12-08 14:59 | 45634.6243 | 2024-12-08 16:51 | 45634.7021 | 0.93102 | 0.0083127 | 282 | 31584 | Unplanned | Adverse weather | Branches on lines due to wind
1112 |  | 1301 | LB ABS G353 |  | Woodbury | 2024-12-08 14:59 | 45634.6243 | 2024-12-08 17:32 | 45634.7306 | 0.30669 | 0.0020045 | 68 | 10404 | Unplanned | Adverse weather | Branches on lines due to wind
1113 |  | 5143 | CB F359- ABS F225 |  | Fairlie Rural | 2024-12-08 15:31 | 45634.6465 | 2024-12-08 16:27 | 45634.6854 | 0.3252 | 0.0058071 | 197 | 11032 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind
1114 |  | 5143 | ABS F225-Fuses F226 |  | Fairlie Rural | 2024-12-08 15:31 | 45634.6465 | 2024-12-08 18:52 | 45634.7861 | 0.22515 | 0.0011202 | 38 | 7638 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind
1115 |  | 5143 | Fuses F226 |  | Fairlie Rural | 2024-12-08 15:31 | 45634.6465 | 2024-12-08 22:28 | 45634.9361 | 0.13521 | 0.00032425 | 11 | 4587 | Unplanned | Adverse weather | Tree on lines and pole replacement due to wind
1116 |  | SRT272 | Fuses T112 |  | Milford | 2024-12-09 09:00 | 45635.375 | 2024-12-09 12:54 | 45635.5375 | 0.11036 | 0.00047164 | 16 | 3744 | Planned | Planned interruption | Replace red tagged pole #01927
1117 |  | SRT272 | Fuses TOD412 |  | Milford | 2024-12-09 09:00 | 45635.375 | 2024-12-09 13:20 | 45635.5556 | 0.022993 | 8.8433e-05 | 3 | 780 | Planned | Planned interruption | Replace red tagged pole #01927
1118 |  | GWM1216 | Fuses L757 |  | Arowhenua | 2024-12-09 09:03 | 45635.3771 | 2024-12-09 12:50 | 45635.5347 | 0.013383 | 5.8955e-05 | 2 | 454 | Planned | Planned interruption | Tree cutting pole #36019
1119 |  | 4622 | Fuses W305 to end |  | Otaio | 2024-12-09 10:00 | 45635.4167 | 2024-12-09 11:31 | 45635.4799 | 0.029507 | 0.00032425 | 11 | 1001 | Unplanned | Adverse weather | Wind - Branch on line
1120 |  | 4418 | Fuses TO B890 |  | Cave | 2024-12-09 14:03 | 45635.5854 | 2024-12-09 15:23 | 45635.641 | 0.0023582 | 2.9478e-05 | 1 | 80 | Unplanned | Defective equipment | Broken 11kV jumper to Tx D890
1121 |  | 4419 | CB L792 - LB L1339 |  | Elginshire | 2024-12-09 14:39 | 45635.6104 | 2024-12-09 15:30 | 45635.6458 | 0.091705 | 0.0017981 | 61 | 3111 | Unplanned | Defective equipment | Loose Jumper @ Links L309
1122 |  | SRT276 | CB T626 |  | Rolleston Road | 2024-12-10 09:00 | 45636.375 | 2024-12-10 09:07 | 45636.3799 | 0.0061903 | 0.00088433 | 30 | 210 | Planned | Planned interruption | ABS T490 replacement
1123 |  | SRT276 | CB T626 |  | Rolleston Road | 2024-12-10 09:00 | 45636.375 | 2024-12-10 16:34 | 45636.6903 | 2.1011 | 0.004628 | 157 | 71278 | Planned | Planned interruption | ABS T490 replacement
1124 |  | SKE1850A | CB13 to RMU E46 |  | Clifton Terrace | 2024-12-10 09:00 | 45636.375 | 2024-12-10 14:55 | 45636.6215 | 1.4755 | 0.0041563 | 141 | 50055 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement
1125 |  | SKE1850A | CB13 to RMU E46 |  | Clifton Terrace | 2024-12-10 09:00 | 45636.375 | 2024-12-10 15:01 | 45636.6257 | 0.053207 | 0.00014739 | 5 | 1805 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement
1126 |  | SKE1850A | CB13 to RMU E46 |  | Clifton Terrace | 2024-12-10 09:00 | 45636.375 | 2024-12-10 15:15 | 45636.6354 | 0.011054 | 2.9478e-05 | 1 | 375 | Planned | Planned interruption | TE26 maintenance & DB P39 replacement
1127 |  | JRM047 | RMU Z449 TOE362 Fuses |  | Pukaki | 2024-12-10 09:05 | 45636.3785 | 2024-12-10 13:27 | 45636.5604 | 0.0077231 | 2.9478e-05 | 1 | 262 | Planned | Planned interruption | Tx E362 oil weep repair
1128 |  | JRM047 | RMU Z449 TOE363 Fuses |  | Pukaki | 2024-12-10 09:05 | 45636.3785 | 2024-12-10 13:29 | 45636.5618 | 0.0077821 | 2.9478e-05 | 1 | 264 | Planned | Planned interruption | Tx E362 oil weep repair
1129 |  | SRT274 | Links W537 |  | Waihuna | 2024-12-10 10:02 | 45636.4181 | 2024-12-10 11:00 | 45636.4583 | 0.0085485 | 0.00014739 | 5 | 290 | Planned | Planned interruption | Repairs pole #31018
1130 |  | 4623 | TX Fuses TO B867 to end |  | Holme Station | 2024-12-10 11:46 | 45636.4903 | 2024-12-10 12:47 | 45636.5326 | 0.0035963 | 5.8955e-05 | 2 | 122 | Unplanned | Defective equipment | Customer pole broken
1131 |  | 4624 | RMU TER38 to end |  | Le Cren Street | 2024-12-10 13:03 | 45636.5437 | 2024-12-10 13:13 | 45636.5507 | 0.056597 | 0.0056597 | 192 | 1920 | Unplanned | Defective equipment | Cable fault
1132 |  | 4624 | RMU TEK4 minus RMU TER38 |  | Le Cren Street | 2024-12-10 13:03 | 45636.5437 | 2024-12-10 13:20 | 45636.5556 | 0.097718 | 0.0057481 | 195 | 3315 | Unplanned | Defective equipment | Cable fault
1133 |  | 4624 | HNT CB5 (Le Cren St) minus RMU TEK4 |  | Le Cren Street | 2024-12-10 13:03 | 45636.5437 | 2024-12-10 13:23 | 45636.5576 | 0.11614 | 0.0058071 | 197 | 3940 | Unplanned | Defective equipment | Cable fault
1134 |  | SRT275 | Fuses W312 Tx A163 |  | Mt Studholme | 2024-12-10 13:30 | 45636.5625 | 2024-12-10 15:15 | 45636.6354 | 0.0061903 | 5.8955e-05 | 2 | 210 | Planned | Planned interruption | Tx A163 Crouch Rd conductor replacement
1135 |  | SRT275 | Fuses W312 |  | Mt Studholme | 2024-12-10 13:30 | 45636.5625 | 2024-12-10 15:01 | 45636.6257 | 0.0080474 | 8.8433e-05 | 3 | 273 | Planned | Planned interruption | Tx A163 Crouch Rd conductor replacement
1136 |  | SRT276 | CB T626 |  | Rolleston Road | 2024-12-10 16:30 | 45636.6875 | 2024-12-10 16:34 | 45636.6903 | 0.0035373 | 0.00088433 | 30 | 120 | Planned | Planned interruption | ABS T490 replacement
1137 |  | DVE395 | Fuses T425 TX D775 |  | Woodbury | 2024-12-11 08:30 | 45637.3542 | 2024-12-11 14:00 | 45637.5833 | 0.0097276 | 2.9478e-05 | 1 | 330 | Planned | Planned interruption | Arundel maintenance Task 12
1138 |  | DVE395 | Fuses T425 TX D319 |  | Woodbury | 2024-12-11 08:30 | 45637.3542 | 2024-12-11 14:12 | 45637.5917 | 0.020163 | 5.8955e-05 | 2 | 684 | Planned | Planned interruption | Arundel maintenance Task 12
1139 |  | DVE395 | Fuses T425 TX D649 |  | Woodbury | 2024-12-11 08:30 | 45637.3542 | 2024-12-11 15:35 | 45637.6493 | 0.012528 | 2.9478e-05 | 1 | 425 | Planned | Planned interruption | Arundel maintenance Task 12
1140 |  | JDJ148 | Fuses TOB756 |  | Pleasant Point Township | 2024-12-11 09:03 | 45637.3771 | 2024-12-11 15:29 | 45637.6451 | 0.011378 | 2.9478e-05 | 1 | 386 | Planned | Planned interruption | Pole #39794 replacement
1141 |  | WMR156 | Fuses TOC404 |  | Fairlie Rural | 2024-12-11 11:49 | 45637.4924 | 2024-12-11 12:03 | 45637.5021 | 0.00041269 | 2.9478e-05 | 1 | 14 | Planned | Planned interruption | Tap change TX C404
1142 |  | 5130 | Pole #31784 to end |  | Morven | 2024-12-11 11:54 | 45637.4958 | 2024-12-11 21:15 | 45637.8854 | 0.066148 | 0.00011791 | 4 | 2244 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles
1143 |  | 5130 | ABS W264 to pole #31784 |  | Morven | 2024-12-11 12:07 | 45637.5049 | 2024-12-11 21:15 | 45637.8854 | 0.38769 | 0.00070746 | 24 | 13152 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles
1144 |  | 5130 | STU CB9 to end minus ABS W264 |  | Morven | 2024-12-11 12:07 | 45637.5049 | 2024-12-11 13:00 | 45637.5417 | 0.50619 | 0.0095508 | 324 | 17172 | Unplanned | Third party interference | Tree fellers dropped tree on lines - broken poles
1145 |  | DVE396 | Links pole #04694 Tx D624 |  | Woodbury | 2024-12-12 08:30 | 45638.3542 | 2024-12-12 14:32 | 45638.6056 | 0.010671 | 2.9478e-05 | 1 | 362 | Planned | Planned interruption | Arundel maintenance Task 13
1146 |  | DVE396 | Links pole #04694 Tx D308 |  | Woodbury | 2024-12-12 08:30 | 45638.3542 | 2024-12-12 15:15 | 45638.6354 | 0.035815 | 8.8433e-05 | 3 | 1215 | Planned | Planned interruption | Arundel maintenance Task 13
1147 |  | DVE397 | Links pole #04534 |  | Woodbury | 2024-12-12 08:30 | 45638.3542 | 2024-12-12 15:51 | 45638.6604 | 0.025999 | 5.8955e-05 | 2 | 882 | Planned | Planned interruption | Arundel maintenance Task 15
1148 |  | JDJ144 | TOB1750 Fuses |  | Elginshire | 2024-12-13 08:30 | 45639.3542 | 2024-12-13 14:18 | 45639.5958 | 0.010258 | 2.9478e-05 | 1 | 348 | Planned | Planned interruption | replace pole #46998
1149 |  | 3880 | Fues TO A16 to end |  | St Andrews | 2024-12-14 23:59 | 45640.9993 | 2024-12-15 09:33 | 45641.3979 | 0.03384 | 5.8955e-05 | 2 | 1148 | Unplanned | Wildlife | Possum on TX A16
1150 |  | DVE398 / GWM1210 | DB4677 to end |  | Woodbury | 2024-12-16 08:30 | 45642.3542 | 2024-12-16 16:15 | 45642.6771 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Arundel Maintenance Task 14
1151 |  | DVE398 / GWM1210 | Fuses TOD312 to end |  | Woodbury | 2024-12-16 08:30 | 45642.3542 | 2024-12-16 16:39 | 45642.6937 | 0.057658 | 0.00011791 | 4 | 1956 | Planned | Planned interruption | Arundel Maintenance Task 14
1152 |  | DVE398 / GWM1210 | Fuses TOD629 to end |  | Woodbury | 2024-12-16 08:30 | 45642.3542 | 2024-12-16 16:59 | 45642.7076 | 0.030008 | 5.8955e-05 | 2 | 1018 | Planned | Planned interruption | Arundel Maintenance Task 14
1153 |  | DVE398 / GWM1210 | ABS T426 - DB4677 - Fuses TOD312 - Fuses TOD629 |  | Woodbury | 2024-12-16 08:30 | 45642.3542 | 2024-12-16 16:00 | 45642.6667 | 1.5255 | 0.0033899 | 115 | 51750 | Planned | Planned interruption | Arundel Maintenance Task 14
1154 |  | SRS026 | ABS F332 to end |  | Fairlie Rural | 2024-12-16 10:04 | 45642.4194 | 2024-12-16 13:38 | 45642.5681 | 0.0063082 | 2.9478e-05 | 1 | 214 | Planned | Planned interruption | Tx C487 replacement
1155 |  | 01202 | TO D269 |  | Speechley | 2024-12-16 15:06 | 45642.6292 | 2024-12-16 15:45 | 45642.6562 | 0.0022993 | 5.8955e-05 | 2 | 78 | Unplanned | Wildlife | Remove Possum from Tx D269
1156 |  | DVE399 | FusesTOD324 to end |  | Woodbury | 2024-12-17 08:30 | 45643.3542 | 2024-12-17 15:05 | 45643.6285 | 0.011644 | 2.9478e-05 | 1 | 395 | Planned | Planned interruption | Arundel Maintenance Task 14
1157 |  | DVE399 | Fuses TOD1816 to end |  | Woodbury | 2024-12-17 08:30 | 45643.3542 | 2024-12-17 15:06 | 45643.6292 | 0.011673 | 2.9478e-05 | 1 | 396 | Planned | Planned interruption | Arundel Maintenance Task 14
1158 |  | DVE399 | Fues TOD323 to end |  | Woodbury | 2024-12-17 08:30 | 45643.3542 | 2024-12-17 15:10 | 45643.6319 | 0.023582 | 5.8955e-05 | 2 | 800 | Planned | Planned interruption | Arundel Maintenance Task 14
1159 |  | DVE399 | ABS T429 - Fuses TOD323 - Fuses TOD1816 - Fuses TOD324 |  | Woodbury | 2024-12-17 08:30 | 45643.3542 | 2024-12-17 14:58 | 45643.6236 | 0.12581 | 0.00032425 | 11 | 4268 | Planned | Planned interruption | Arundel Maintenance Task 14
1160 |  | SRS028 | DB2787 to end |  | Highfield | 2024-12-17 08:44 | 45643.3639 | 2024-12-17 15:05 | 45643.6285 | 0.022462 | 5.8955e-05 | 2 | 762 | Planned | Planned interruption | DB Removal
1161 |  | SRS028 | Fuses TOB1186 - DB2787 |  | Highfield | 2024-12-17 08:44 | 45643.3639 | 2024-12-17 16:55 | 45643.7049 | 0.028947 | 5.8955e-05 | 2 | 982 | Planned | Planned interruption | DB Removal
1162 |  | GWM1227 | ABS T450 to end |  | Rangitata | 2024-12-17 09:00 | 45643.375 | 2024-12-17 11:58 | 45643.4986 | 0.19939 | 0.0011202 | 38 | 6764 | Planned | Planned interruption | Tree trimming
1163 |  | SKE1759 | Tx E212'01' to end |  | Lakeside Drive | 2024-12-17 09:17 | 45643.3868 | 2024-12-17 15:23 | 45643.641 | 0.36682 | 0.0010022 | 34 | 12444 | Planned | Planned interruption | RMU maintenance
1164 |  | SKE1759 | Tx E254-02 |  | Lakeside Drive | 2024-12-17 09:17 | 45643.3868 | 2024-12-17 15:29 | 45643.6451 | 0.010966 | 2.9478e-05 | 1 | 372 | Planned | Planned interruption | RMU maintenance
1165 |  | 4625 | Fuses TO B1159 to end |  | Arowhenua | 2024-12-17 11:26 | 45643.4764 | 2024-12-17 12:29 | 45643.5201 | 0.0018571 | 2.9478e-05 | 1 | 63 | Unplanned | Unknown | Unknown - 2x blown DO's
1166 |  | 5145 | TX B1110 CCT7 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 09:58 | 45644.4153 | 0.045101 | 0.0002653 | 9 | 1530 | Unplanned | Defective equipment | Blown pothead pole #24243
1167 |  | 5145 | TX B1110 CCT6 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 10:03 | 45644.4187 | 0.051586 | 0.00029478 | 10 | 1750 | Unplanned | Defective equipment | Blown pothead pole #24243
1168 |  | 5145 | TX B1110 CCT4 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 11:41 | 45644.4868 | 0.072427 | 0.0002653 | 9 | 2457 | Unplanned | Defective equipment | Blown pothead pole #24243
1169 |  | 5145 | TX B1110 CCT2 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 11:44 | 45644.4889 | 0.089494 | 0.00032425 | 11 | 3036 | Unplanned | Defective equipment | Blown pothead pole #24243
1170 |  | 5145 | TX B1110 CCT3 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 11:44 | 45644.4889 | 0.09763 | 0.00035373 | 12 | 3312 | Unplanned | Defective equipment | Blown pothead pole #24243
1171 |  | 5145 | TX B1110 CCT5 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 11:45 | 45644.4896 | 0.073488 | 0.0002653 | 9 | 2493 | Unplanned | Defective equipment | Blown pothead pole #24243
1172 |  | 5145 | TX B1110 01 |  | Washdyke | 2024-12-18 07:08 | 45644.2972 | 2024-12-18 11:41 | 45644.4868 | 0.0080474 | 2.9478e-05 | 1 | 273 | Unplanned | Defective equipment | Blown pothead pole #24243
1173 |  | DVE400 | TX D322'01' |  | Woodbury | 2024-12-18 08:41 | 45644.3618 | 2024-12-18 15:12 | 45644.6333 | 0.046103 | 0.00011791 | 4 | 1564 | Planned | Planned interruption | Arundel Maintenance Task 15
1174 |  | 3792 | CB W366 - W560 |  | Otaio | 2024-12-18 19:01 | 45644.7924 | 2024-12-18 19:23 | 45644.8076 | 0.21012 | 0.0095508 | 324 | 7128 | Unplanned | Wildlife | Lines down due to bird strike
1175 |  | 3792 | W560 |  | Otaio | 2024-12-18 19:01 | 45644.7924 | 2024-12-18 21:23 | 45644.891 | 0.054416 | 0.00038321 | 13 | 1846 | Unplanned | Wildlife | Lines down due to bird strike
1176 |  | SRT281 | Tx B544'01' |  | Holme Station | 2024-12-19 09:24 | 45645.3917 | 2024-12-19 10:57 | 45645.4563 | 0.0054828 | 5.8955e-05 | 2 | 186 | Planned | Planned interruption | Transformer replacement
1177 |  | SRT281 | ABS L134 to end |  | Holme Station | 2024-12-19 09:24 | 45645.3917 | 2024-12-19 10:44 | 45645.4472 | 0.042448 | 0.0005306 | 18 | 1440 | Planned | Planned interruption | Transformer replacement
1178 |  | SRT281 | Links L132 - ABS L134 - Tx B544'01' |  | Holme Station | 2024-12-19 09:24 | 45645.3917 | 2024-12-19 10:41 | 45645.4451 | 0.043126 | 0.00056008 | 19 | 1463 | Planned | Planned interruption | Transformer replacement
1179 |  | SRT282 | TX B338 01 |  | Cave | 2024-12-19 10:00 | 45645.4167 | 2024-12-19 11:36 | 45645.4833 | 0.0028299 | 2.9478e-05 | 1 | 96 | Planned | Planned interruption | Transformer replacement
1180 |  | 5145 | Gen OFF Tx B1110 (CCT 2, 3, 5 & ICP off bus) - Restore |  | Washdyke | 2024-12-20 10:40 | 45646.4444 | 2024-12-20 10:44 | 45646.4472 | 0.0038911 | 0.00097276 | 33 | 132 | Unplanned | Defective equipment | Blown pothead pole #24243
1181 |  | 5145 | Gen OFF Tx B1110 CCT 4 - Restore |  | Washdyke | 2024-12-20 10:40 | 45646.4444 | 2024-12-20 11:12 | 45646.4667 | 0.0084896 | 0.0002653 | 9 | 288 | Unplanned | Defective equipment | Blown pothead pole #24243
1182 |  | 3793 | L808 - L1342 |  | Hadlow | 2024-12-20 17:04 | 45646.7111 | 2024-12-20 17:12 | 45646.7167 | 0.035845 | 0.0044806 | 152 | 1216 | Unplanned | Third party interference | Car v Pole
1183 |  | 3793 | L1342 - LX99 |  | Hadlow | 2024-12-20 17:10 | 45646.7153 | 2024-12-20 17:20 | 45646.7222 | 0.015918 | 0.0015918 | 54 | 540 | Unplanned | Third party interference | Car v Pole
1184 |  | 3793 | LX99 - L710 |  | Hadlow | 2024-12-20 17:10 | 45646.7153 | 2024-12-20 20:35 | 45646.8576 | 0.51969 | 0.0025351 | 86 | 17630 | Unplanned | Third party interference | Car v Pole
1185 |  | 3795 | F380 |  | Fairlie Rural | 2024-12-21 16:29 | 45647.6868 | 2024-12-21 18:01 | 45647.7507 | 2.0963 | 0.022786 | 773 | 71116 | Unplanned | Lighting | Lightning
1186 |  | 4626 | Fuses TOD1960 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 18:13 | 45647.759 | 0.0026235 | 2.9478e-05 | 1 | 89 | Unplanned | Lighting | Lightning storm Tripp Settlement
1187 |  | 4626 | Fuses TOD383 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 18:26 | 45647.7681 | 0.0030067 | 2.9478e-05 | 1 | 102 | Unplanned | Lighting | Lightning storm Tripp Settlement
1188 |  | 4626 | Fuses G159 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 18:51 | 45647.7854 | 0.022462 | 0.00017687 | 6 | 762 | Unplanned | Lighting | Lightning storm Tripp Settlement
1189 |  | 4626 | Fuses TOD298 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 19:22 | 45647.8069 | 0.0046575 | 2.9478e-05 | 1 | 158 | Unplanned | Lighting | Lightning storm Tripp Settlement
1190 |  | 4626 | Fuses TOD978 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 19:45 | 45647.8229 | 0.0053355 | 2.9478e-05 | 1 | 181 | Unplanned | Lighting | Lightning storm Tripp Settlement
1191 |  | 4626 | Fuses TOD865 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 20:05 | 45647.8368 | 0.005925 | 2.9478e-05 | 1 | 201 | Unplanned | Lighting | Lightning storm Tripp Settlement
1192 |  | 4626 | Fuses TOD380 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-21 20:17 | 45647.8451 | 0.0062787 | 2.9478e-05 | 1 | 213 | Unplanned | Lighting | Lightning storm Tripp Settlement
1193 |  | 4626 | Fuses TOD294 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-22 08:14 | 45648.3431 | 0.21931 | 0.00023582 | 8 | 7440 | Unplanned | Lighting | Lightning storm Tripp Settlement
1194 |  | 4626 | Fuses TOD379 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-22 10:36 | 45648.4417 | 0.0316 | 2.9478e-05 | 1 | 1072 | Unplanned | Lighting | Lightning storm Tripp Settlement
1195 |  | 4626 | Fuses TOD947 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-22 10:36 | 45648.4417 | 0.0316 | 2.9478e-05 | 1 | 1072 | Unplanned | Lighting | Lightning storm Tripp Settlement
1196 |  | 4626 | Fuses TOD1150 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-22 12:11 | 45648.5076 | 0.068801 | 5.8955e-05 | 2 | 2334 | Unplanned | Lighting | Lightning storm Tripp Settlement
1197 |  | 4626 | Fuses TOD297 |  | Woodbury | 2024-12-21 16:44 | 45647.6972 | 2024-12-22 12:38 | 45648.5264 | 0.035196 | 2.9478e-05 | 1 | 1194 | Unplanned | Lighting | Lightning storm Tripp Settlement
1198 |  | 4626 | LBS G353 |  | Woodbury | 2024-12-22 08:38 | 45648.3597 | 2024-12-22 10:27 | 45648.4354 | 0.20564 | 0.0018866 | 64 | 6976 | Unplanned | Lighting | Lightning storm Tripp Settlement
1199 |  | 3882 | CB T626 minus LBS T775 |  | Rolleston Road | 2024-12-24 22:30 | 45650.9375 | 2024-12-24 22:39 | 45650.9437 | 0.010347 | 0.0011496 | 39 | 351 | Unplanned | Wildlife | Bird Strike
1200 |  | 3882 | LBS T775 minus ABS T675 |  | Rolleston Road | 2024-12-24 22:30 | 45650.9375 | 2024-12-24 23:49 | 45650.9924 | 0.33301 | 0.0042153 | 143 | 11297 | Unplanned | Wildlife | Bird Strike
1201 |  | 3882 | ABS T675 to end |  | Rolleston Road | 2024-12-24 22:30 | 45650.9375 | 2024-12-25 03:51 | 45651.1604 | 0.047312 | 0.00014739 | 5 | 1605 | Unplanned | Wildlife | Bird Strike
1202 |  | 3881 | ABS M385 to end |  | Haldon-Lilybank 22kV | 2024-12-28 08:31 | 45654.3549 | 2024-12-28 09:58 | 45654.4153 | 0.041033 | 0.00047164 | 16 | 1392 | Unplanned | Defective equipment | Reported defect - Missing Arm brace bolts
1203 |  | 3796 | CB6 - L166 |  | Normanby | 2024-12-31 18:44 | 45657.7806 | 2024-12-31 19:51 | 45657.8271 | 0.7031 | 0.010494 | 356 | 23852 | Unplanned | Unknown | Unknown
1204 |  | 3796 | L166 - L1220 |  | Normanby | 2024-12-31 18:44 | 45657.7806 | 2024-12-31 20:12 | 45657.8417 | 0.23606 | 0.0026825 | 91 | 8008 | Unplanned | Unknown | Unknown
1205 |  | 3796 | L1220 |  | Normanby | 2024-12-31 18:44 | 45657.7806 | 2024-12-31 20:13 | 45657.8424 | 0.33056 | 0.0037142 | 126 | 11214 | Unplanned | Unknown | Unknown
1206 |  | 3797 | T626 - T665 |  | Rolleston Road | 2025-01-01 13:42 | 45658.5708 | 2025-01-01 14:30 | 45658.6042 | 0.24337 | 0.0050702 | 172 | 8256 | Unplanned | Wildlife | Bird strike - Lines down
1207 |  | 3797 | T665 |  | Rolleston Road | 2025-01-01 13:42 | 45658.5708 | 2025-01-01 16:03 | 45658.6687 | 0.062345 | 0.00044216 | 15 | 2115 | Unplanned | Wildlife | Bird strike - Lines down
1208 |  | 3797 | Temp Fuses P#08511 |  | Winchester | 2025-01-05 04:56 | 45662.2056 | 2025-01-05 06:35 | 45662.2743 | 0.014591 | 0.00014739 | 5 | 495 | Unplanned | Vegetation | Tree on line @ P#08525
1209 |  | SLA687 | Fuses TO C355 |  | Fairlie Rural | 2025-01-06 08:02 | 45663.3347 | 2025-01-06 08:06 | 45663.3375 | 0.0011791 | 0.00029478 | 10 | 40 | Planned | Planned interruption | Retap Tx C355
1210 |  | 5146 | TOD63 |  | Mahan Road | 2025-01-06 11:03 | 45663.4604 | 2025-01-06 15:06 | 45663.6292 | 0.028652 | 0.00011791 | 4 | 972 | Unplanned | Vegetation | Tree on line at p #06518
1211 |  | 5147 | L187 |  | Holme Station | 2025-01-07 11:28 | 45664.4778 | 2025-01-07 16:05 | 45664.6701 | 0.016331 | 5.8955e-05 | 2 | 554 | Unplanned | Vegetation | Trees on line @ P#43786
1212 |  | 5149 | PLP CB4 to end |  | Totara Valley | 2025-01-07 19:47 | 45664.8243 | 2025-01-07 20:27 | 45664.8521 | 0.68152 | 0.017038 | 578 | 23120 | Unplanned | Adverse weather | Tree branch on line at pole #40317
1213 |  | 5148 | GLD G191 to G237 |  | Geraldine Township | 2025-01-07 20:09 | 45664.8396 | 2025-01-07 21:02 | 45664.8764 | 2.0623 | 0.038911 | 1320 | 69960 | Unplanned | Adverse weather | Unkown - Possible trees near lines touching due to winds
1214 |  | 5148 | G237 to end |  | Geraldine Township | 2025-01-07 20:09 | 45664.8396 | 2025-01-07 21:21 | 45664.8896 | 0.43721 | 0.0060724 | 206 | 14832 | Unplanned | Adverse weather | Unkown - Possible trees near lines touching due to winds
1215 |  | 4628 | Fuses W503 |  | Waikakahi | 2025-01-10 00:10 | 45667.0069 | 2025-01-10 00:49 | 45667.034 | 0.0068978 | 0.00017687 | 6 | 234 | Unplanned | Wildlife | Bird Strke
1216 |  | 4629 | CB3 - T642 |  | Mahan Road | 2025-01-11 17:32 | 45668.7306 | 2025-01-11 19:29 | 45668.8118 | 0.082773 | 0.00070746 | 24 | 2808 | Unplanned | Defective equipment | Lines down near pole #05365
1217 |  | 4629 | ABS T642 - T464 |  | Mahan Road | 2025-01-11 17:32 | 45668.7306 | 2025-01-11 17:53 | 45668.7451 | 0.042094 | 0.0020045 | 68 | 1428 | Unplanned | Defective equipment | Lines down near pole #05365
1218 |  | 4651 | Fuses TO B5 |  | St Andrews | 2025-01-15 19:53 | 45672.8285 | 2025-01-16 00:15 | 45673.0104 | 0.0077231 | 2.9478e-05 | 1 | 262 | Unplanned | Defective equipment | Broken Insulator
1219 |  | HTR075 | Fuses L804 TO END |  | Hadlow | 2025-01-20 08:30 | 45677.3542 | 2025-01-20 12:57 | 45677.5396 | 0.38566 | 0.0014444 | 49 | 13083 | Planned | Planned interruption | Tree Trimming
1220 |  | HTR076 | ABS L347 - Fuses L341 - ABS L346 |  | Waitawa | 2025-01-20 08:54 | 45677.3708 | 2025-01-20 12:53 | 45677.5368 | 0.1409 | 0.00058955 | 20 | 4780 | Planned | Planned interruption | Tree Trimming
1221 |  | HTR078 | Fuses TO B1086 |  | Waipopo | 2025-01-21 08:30 | 45678.3542 | 2025-01-21 12:15 | 45678.5104 | 0.013265 | 5.8955e-05 | 2 | 450 | Planned | Planned interruption | Tree Trimming
1222 |  | HTR077 | ABS L878 TO END |  | Normanby | 2025-01-21 08:30 | 45678.3542 | 2025-01-21 11:55 | 45678.4965 | 0.12086 | 0.00058955 | 20 | 4100 | Planned | Planned interruption | Tree Trimming
1223 |  | SKE1910 | Fuses T0 B600 + Fuses TO B638 |  | Highfield | 2025-01-21 08:30 | 45678.3542 | 2025-01-21 17:04 | 45678.7111 | 1.3939 | 0.0027119 | 92 | 47288 | Planned | Planned interruption | New RMU Installation
1224 |  | ACD184 | Fuses T573 - Fuses TO D910 |  | Winchester | 2025-01-21 09:00 | 45678.375 | 2025-01-21 15:11 | 45678.6326 | 0.032809 | 8.8433e-05 | 3 | 1113 | Planned | Planned interruption | Pole Replacement
1225 |  | ACD184 | Fuses TO D910 |  | Winchester | 2025-01-21 09:00 | 45678.375 | 2025-01-21 15:36 | 45678.65 | 0.023346 | 5.8955e-05 | 2 | 792 | Planned | Planned interruption | Pole Replacement
1226 |  | JRM050 | Fuses TO B1964 |  | Totara Valley | 2025-01-21 09:00 | 45678.375 | 2025-01-21 12:05 | 45678.5035 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Transformer maintenance
1227 |  | SLA694 | ABS W557 |  | Tawai | 2025-01-21 09:27 | 45678.3938 | 2025-01-21 13:28 | 45678.5611 | 0.042625 | 0.00017687 | 6 | 1446 | Unplanned | Third party interference | Safety Disconnect
1228 |  | SKE1911 | Fuses To B686 |  | Highfield | 2025-01-22 08:33 | 45679.3562 | 2025-01-22 15:16 | 45679.6361 | 0.89096 | 0.0022108 | 75 | 30225 | Planned | Planned interruption | New RMU Installation
1229 |  | JDJ151 | Fuses TO D306 |  | Woodbury | 2025-01-22 09:31 | 45679.3965 | 2025-01-22 14:30 | 45679.6042 | 0.0088138 | 2.9478e-05 | 1 | 299 | Planned | Planned interruption | Pole Replacement
1230 |  | SKE1912 | Fuses TO B685 + Fuses To B1349 |  | Highfield | 2025-01-23 08:00 | 45680.3333 | 2025-01-23 16:08 | 45680.6722 | 0.79118 | 0.0016213 | 55 | 26840 | Planned | Planned interruption | New RMU Installation
1231 |  | SKE1912 | Pole #27844 to end |  | Highfield | 2025-01-23 08:00 | 45680.3333 | 2025-01-23 16:14 | 45680.6764 | 0.058248 | 0.00011791 | 4 | 1976 | Planned | Planned interruption | New RMU Installation
1232 |  | SKE1912 | Fuses To B1425 |  | Highfield | 2025-01-23 08:00 | 45680.3333 | 2025-01-23 16:16 | 45680.6778 | 0.014621 | 2.9478e-05 | 1 | 496 | Planned | Planned interruption | New RMU Installation
1233 |  | SKE1912 | Tx B686-02 |  | Highfield | 2025-01-23 08:06 | 45680.3375 | 2025-01-23 15:36 | 45680.65 | 0.4908 | 0.0010907 | 37 | 16650 | Planned | Planned interruption | New RMU Installation
1234 |  | SKE1904 | TO B1332 - 251 Wai-Iti (P#27656) - 4 Broadway (P#27656) |  | Highfield | 2025-01-25 07:30 | 45682.3125 | 2025-01-25 18:30 | 45682.7708 | 1.3035 | 0.001975 | 67 | 44220 | Planned | Planned interruption | Pages to Centennial OH to UG
1235 |  | SKE1904 | 251 Wai-Iti (P#27656) + 4 Broadway (P#27656) |  | Highfield | 2025-01-25 07:30 | 45682.3125 | 2025-01-25 19:06 | 45682.7958 | 0.041033 | 5.8955e-05 | 2 | 1392 | Planned | Planned interruption | Pages to Centennial OH to UG
1236 |  | SKE1904 | LB45 |  | Highfield | 2025-01-25 07:34 | 45682.3153 | 2025-01-25 18:33 | 45682.7729 | 0.25254 | 0.00038321 | 13 | 8567 | Planned | Planned interruption | Pages to Centennial OH to UG
1237 |  | SKE1904 | P#27642 + P#54685 + 293 Wai-Iti (P#27646) - 2-13 Morgans Rd (P#27643) - 11A Morgans Rd (P#27643) - 11C Morgans Rd (P#27643) - 305 Wai-Iti (P#27643) - 307 Wai-Iti (P#27643) - 289 Wai-Iti (P#27646) - 291 Wai-Iti (P#27646) - 293 Wai-Iti (P#27646) - 295 Wai-Iti (P#27646) |  | Highfield | 2025-01-25 07:35 | 45682.316 | 2025-01-25 18:41 | 45682.7785 | 0.45154 | 0.00067799 | 23 | 15318 | Planned | Planned interruption | Pages to Centennial OH to UG
1238 |  | SKE1904 | 307 Wai-Iti (P#27643) |  | Highfield | 2025-01-25 07:35 | 45682.316 | 2025-01-25 18:47 | 45682.7826 | 0.019809 | 2.9478e-05 | 1 | 672 | Planned | Planned interruption | Pages to Centennial OH to UG
1239 |  | SKE1904 | 305 Wai-Iti (P#27643) + 2-13 Morgans Rd (P#27643) + 11A Morgans Rd (P#27643) + 11C Morgans Rd (P#27643) |  | Highfield | 2025-01-25 07:35 | 45682.316 | 2025-01-25 18:49 | 45682.784 | 0.079472 | 0.00011791 | 4 | 2696 | Planned | Planned interruption | Pages to Centennial OH to UG
1240 |  | SKE1904 | 289 Wai-Iti (P#27646) + 291 Wai-Iti (P#27646) + 293 Wai-Iti (P#27646) + 295 Wai-Iti (P#27646) |  | Highfield | 2025-01-25 07:35 | 45682.316 | 2025-01-25 18:57 | 45682.7896 | 0.080415 | 0.00011791 | 4 | 2728 | Planned | Planned interruption | Pages to Centennial OH to UG
1241 |  | 4752 | RGA CB3 |  | Mahan Road | 2025-01-26 07:00 | 45683.2917 | 2025-01-26 11:16 | 45683.4694 | 0.69426 | 0.0027119 | 92 | 23552 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386
1242 |  | 4751 | CB T127 |  | Rangitata | 2025-01-26 07:01 | 45683.2924 | 2025-01-26 09:47 | 45683.4076 | 0.3621 | 0.0021813 | 74 | 12284 | Unplanned | Third party interference | Irrigator spraying lines
1243 |  | 4752 | RGA CB3-ABS T642 |  | Mahan Road | 2025-01-26 19:10 | 45683.7986 | 2025-01-27 01:57 | 45684.0813 | 0.28794 | 0.00070746 | 24 | 9768 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386
1244 |  | 4752 | ABS T642 |  | Mahan Road | 2025-01-26 19:10 | 45683.7986 | 2025-01-26 20:54 | 45683.8708 | 0.20847 | 0.0020045 | 68 | 7072 | Unplanned | Defective equipment | Broken insulator and LAs pole #05386
1245 |  | 1203 | TIM CB2832 |  | Grants Road | 2025-01-27 05:54 | 45684.2458 | 2025-01-27 06:05 | 45684.2535 | 0.37451 | 0.034047 | 1155 | 12705 | Unplanned | Third party interference | Isolation for Car V Pole
1246 |  | SKE1760A | L425 |  | Old North Road | 2025-01-27 08:03 | 45684.3354 | 2025-01-29 17:10 | 45686.7153 | 0.10102 | 2.9478e-05 | 1 | 3427 | Planned | Planned interruption | RMU Maintenance
1247 |  | SKE1760A | L426 |  | Old North Road | 2025-01-27 08:03 | 45684.3354 | 2025-01-29 17:20 | 45686.7222 | 0.20263 | 5.8955e-05 | 2 | 6874 | Planned | Planned interruption | RMU Maintenance
1248 |  | 5132 | RMU M146 to end |  | Lakeside Drive | 2025-01-27 16:19 | 45684.6799 | 2025-01-27 18:54 | 45684.7875 | 0.018276 | 0.00011791 | 4 | 620 | Unplanned | Defective equipment | Damaged insulation on RMU Bushing
1249 |  | 5132 | RMU M101 to end minus M146 |  | Lakeside Drive | 2025-01-27 18:40 | 45684.7778 | 2025-01-27 18:54 | 45684.7875 | 0.00041269 | 2.9478e-05 | 1 | 14 | Unplanned | Defective equipment | Damaged insulation on RMU Bushing
1250 |  | ACD175 | G177 (LBS G353) - D2158 (Ex. Tx D865) - D947 - D1126 - D297 |  | Woodbury | 2025-01-28 08:31 | 45685.3549 | 2025-01-28 16:43 | 45685.6965 | 0.91369 | 0.0018571 | 63 | 30996 | Planned | Planned interruption | Tripp Settlement Line maintenance
1251 |  | ACD175 | D2158 (Ex. Tx D865) |  | Woodbury | 2025-01-28 08:31 | 45685.3549 | 2025-01-28 17:06 | 45685.7125 | 0.015181 | 2.9478e-05 | 1 | 515 | Planned | Planned interruption | Tripp Settlement Line maintenance
1252 |  | ACD175 | D947 |  | Woodbury | 2025-01-28 08:31 | 45685.3549 | 2025-01-28 17:19 | 45685.7215 | 0.015564 | 2.9478e-05 | 1 | 528 | Planned | Planned interruption | Tripp Settlement Line maintenance
1253 |  | ACD175 | D1126 |  | Woodbury | 2025-01-28 08:31 | 45685.3549 | 2025-01-28 17:28 | 45685.7278 | 0.031659 | 5.8955e-05 | 2 | 1074 | Planned | Planned interruption | Tripp Settlement Line maintenance
1254 |  | ACD175 | D297 |  | Woodbury | 2025-01-28 08:31 | 45685.3549 | 2025-01-28 17:43 | 45685.7382 | 0.016272 | 2.9478e-05 | 1 | 552 | Planned | Planned interruption | Tripp Settlement Line maintenance
1255 |  | 5150 | RMU L352 |  | Elginshire | 2025-01-28 13:12 | 45685.55 | 2025-01-28 15:11 | 45685.6326 | 0.0035078 | 2.9478e-05 | 1 | 119 | Unplanned | Unknown | Tap Tx B1346 down to Tap #1
1256 |  | 5133 | CB W590 to end minus ABS W494 |  | Tawai | 2025-01-28 21:15 | 45685.8854 | 2025-01-28 21:52 | 45685.9111 | 0.18651 | 0.0050407 | 171 | 6327 | Unplanned | Unknown | Broken Conductor - Possible corrosion from PG Clamp
1257 |  | 5133 | ABS W494 to end |  | Tawai | 2025-01-28 21:15 | 45685.8854 | 2025-01-29 00:04 | 45686.0028 | 0.45832 | 0.0027119 | 92 | 15548 | Unplanned | Unknown | Broken Conductor - Possible corrosion from PG Alamp
1258 |  | ACD176 | G177 (LBS G353) |  | Woodbury | 2025-01-29 08:30 | 45686.3542 | 2025-01-29 15:48 | 45686.6583 | 0.87796 | 0.0020045 | 68 | 29784 | Planned | Planned interruption | Tripp Settlement Line maintenance
1259 |  | GWM1236 | LX82 |  | Hadlow | 2025-01-29 09:00 | 45686.375 | 2025-01-29 11:42 | 45686.4875 | 0.19579 | 0.0012086 | 41 | 6642 | Planned | Planned interruption | Tree Cutting
1260 |  | 5131 | GLD CB G191 to end minus TX D373 |  | Geraldine Township | 2025-01-29 17:16 | 45686.7194 | 2025-01-29 18:06 | 45686.7542 | 2.2403 | 0.044806 | 1520 | 76000 | Unplanned | Third party interference | Emergency Trip - Lines down - Woodbury Rd
1261 |  | 5131 | TX D373 |  | Geraldine Township | 2025-01-29 17:16 | 45686.7194 | 2025-01-29 19:19 | 45686.8049 | 0.021755 | 0.00017687 | 6 | 738 | Unplanned | Third party interference | Emergency Trip - Lines down - Woodbury Rd
1262 |  | ACD177 | G162 - D298 - D378 |  | Woodbury | 2025-01-30 08:30 | 45687.3542 | 2025-01-30 14:30 | 45687.6042 | 0.042448 | 0.00011791 | 4 | 1440 | Planned | Planned interruption | Tripp Settlement Line maintenance
1263 |  | ACD177 | D298 |  | Woodbury | 2025-01-30 08:30 | 45687.3542 | 2025-01-30 14:42 | 45687.6125 | 0.010966 | 2.9478e-05 | 1 | 372 | Planned | Planned interruption | Tripp Settlement Line maintenance
1264 |  | ACD177 | D378 |  | Woodbury | 2025-01-30 08:30 | 45687.3542 | 2025-01-30 15:02 | 45687.6264 | 0.02311 | 5.8955e-05 | 2 | 784 | Planned | Planned interruption | Tripp Settlement Line maintenance
1265 |  | 3884 | Fuses W266 to end |  | Morven | 2025-02-01 21:53 | 45689.9118 | 2025-02-01 23:48 | 45689.9917 | 0.030509 | 0.0002653 | 9 | 1035 | Unplanned | Unknown | Unknown
1266 |  | 3883 | Fuses L208 to end |  | Levels Plain | 2025-02-02 06:05 | 45690.2535 | 2025-02-02 07:23 | 45690.3076 | 0.041387 | 0.0005306 | 18 | 1404 | Unplanned | Wildlife | Bird strike
1267 |  | SEM099 | Fuses TO A1053 to end |  | Glenavy | 2025-02-03 09:04 | 45691.3778 | 2025-02-03 16:19 | 45691.6799 | 0.025646 | 5.8955e-05 | 2 | 870 | Planned | Planned interruption | Tree Cutting
1268 |  | SRS031 | TE140 CCT14 to end |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-03 18:36 | 45691.775 | 0.0022108 | 8.8433e-05 | 3 | 75 | Planned | Planned interruption | Lucy Box Replacement
1269 |  | SRS031 | TE140 CCT15 to end minus conduit box H253 to end |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-03 18:29 | 45691.7701 | 0.0015918 | 8.8433e-05 | 3 | 54 | Planned | Planned interruption | Lucy Box Replacement
1270 |  | SRS031 | Conduit box H253 to end |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-03 18:35 | 45691.7743 | 0.0028299 | 0.00011791 | 4 | 96 | Planned | Planned interruption | Lucy Box Replacement
1271 |  | SRS031 | TE140 CCT16 to end |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-03 18:36 | 45691.775 | 0.0051586 | 0.00020634 | 7 | 175 | Planned | Planned interruption | Lucy Box Replacement
1272 |  | SRS031 | TE140 CCT17 to end |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-03 18:41 | 45691.7785 | 0.0035373 | 0.00011791 | 4 | 120 | Planned | Planned interruption | Lucy Box Replacement
1273 |  | SRS031 | TE140 CCT13 - New LB H359 - 1 (H251) |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-04 04:05 | 45692.1701 | 0.052529 | 8.8433e-05 | 3 | 1782 | Planned | Planned interruption | Lucy Box Replacement
1274 |  | SRS031 | TE140 CCT13 - New LB H359 - 1 (H250) |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-04 04:32 | 45692.1889 | 0.036611 | 5.8955e-05 | 2 | 1242 | Planned | Planned interruption | Lucy Box Replacement
1275 |  | SRS031 | TE140 CCT13 - New LB H359 - 2 |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-04 04:38 | 45692.1931 | 0.018482 | 2.9478e-05 | 1 | 627 | Planned | Planned interruption | Lucy Box Replacement
1276 |  | SRS031 | TE140 CCT13 - New LB H359 - 7 |  | Le Cren Street | 2025-02-03 18:11 | 45691.7576 | 2025-02-04 03:52 | 45692.1611 | 0.034253 | 5.8955e-05 | 2 | 1162 | Planned | Planned interruption | Lucy Box Replacement
1277 |  | SRS031 | TE140 CCT15 to end minus conduit box H253 to end |  | Le Cren Street | 2025-02-04 03:21 | 45692.1396 | 2025-02-04 03:43 | 45692.1549 | 0.0019455 | 8.8433e-05 | 3 | 66 | Planned | Planned interruption | Lucy Box Replacement
1278 |  | SRS031 | TE140 CCT17 to end |  | Le Cren Street | 2025-02-04 03:21 | 45692.1396 | 2025-02-04 03:43 | 45692.1549 | 0.002594 | 0.00011791 | 4 | 88 | Planned | Planned interruption | Lucy Box Replacement
1279 |  | SRS031 | Conduit box H253 to end |  | Le Cren Street | 2025-02-04 03:23 | 45692.141 | 2025-02-04 03:43 | 45692.1549 | 0.0023582 | 0.00011791 | 4 | 80 | Planned | Planned interruption | Lucy Box Replacement
1280 |  | SRS031 | TE140 CCT14 to end |  | Le Cren Street | 2025-02-04 03:25 | 45692.1424 | 2025-02-04 03:43 | 45692.1549 | 0.0015918 | 8.8433e-05 | 3 | 54 | Planned | Planned interruption | Lucy Box Replacement
1281 |  | SRS031 | TE140 CCT16 to end |  | Le Cren Street | 2025-02-04 03:25 | 45692.1424 | 2025-02-04 03:43 | 45692.1549 | 0.0037142 | 0.00020634 | 7 | 126 | Planned | Planned interruption | Lucy Box Replacement
1282 |  | 5075 | T644 |  | Arundel | 2025-02-04 06:09 | 45692.2562 | 2025-02-04 07:07 | 45692.2965 | 0.0051291 | 8.8433e-05 | 3 | 174 | Unplanned | Unknown | Unknown
1283 |  | ACD178 | Fuses G163 to end minus TX D380, D381, D1163, D978, D1150 |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 15:43 | 45692.6549 | 0.038291 | 8.8433e-05 | 3 | 1299 | Planned | Planned interruption | Lines Maintenance
1284 |  | ACD178 | TX D380 to end |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 16:02 | 45692.6681 | 0.013324 | 2.9478e-05 | 1 | 452 | Planned | Planned interruption | Lines Maintenance
1285 |  | ACD178 | TX D381 to end |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 16:23 | 45692.6826 | 0.013943 | 2.9478e-05 | 1 | 473 | Planned | Planned interruption | Lines Maintenance
1286 |  | ACD178 | TX D1163 to end |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 16:15 | 45692.6771 | 0.013707 | 2.9478e-05 | 1 | 465 | Planned | Planned interruption | Lines Maintenance
1287 |  | ACD178 | TX D978 to end |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 16:29 | 45692.6868 | 0.01412 | 2.9478e-05 | 1 | 479 | Planned | Planned interruption | Lines Maintenance
1288 |  | ACD178 | TX D1150 to end |  | Woodbury | 2025-02-04 08:30 | 45692.3542 | 2025-02-04 16:57 | 45692.7063 | 0.02989 | 5.8955e-05 | 2 | 1014 | Planned | Planned interruption | Lines Maintenance
1289 |  | LXL128A | TE19 - TE19-11 |  | Park Lane | 2025-02-04 20:22 | 45692.8486 | 2025-02-04 21:44 | 45692.9056 | 0.21271 | 0.002594 | 88 | 7216 | Unplanned | Defective equipment | Cable fault
1290 |  | LXL128A | TE19-11 - DB Z57 |  | Park Lane | 2025-02-04 20:22 | 45692.8486 | 2025-02-04 22:17 | 45692.9285 | 0.027119 | 0.00023582 | 8 | 920 | Unplanned | Defective equipment | Cable fault
1291 |  | LXL128A | DB Z57 |  | Park Lane | 2025-02-04 20:22 | 45692.8486 | 2025-02-04 21:50 | 45692.9097 | 0.0051881 | 5.8955e-05 | 2 | 176 | Unplanned | Defective equipment | Cable fault
1292 |  | GWM1241 | ABS T665 to end |  | Rolleston Road | 2025-02-05 09:00 | 45693.375 | 2025-02-05 11:12 | 45693.4667 | 0.058366 | 0.00044216 | 15 | 1980 | Planned | Planned interruption | Tree cutting
1293 |  | WMR163 | BPD13 - ABS WX46 |  | Waikakahi | 2025-02-06 03:53 | 45694.1618 | 2025-02-06 05:53 | 45694.2451 | 0.21578 | 0.0017981 | 61 | 7320 | Unplanned | Unknown | Unknown
1294 |  | WMR163 | BPD13 - ABS W117 |  | Waikakahi | 2025-02-06 03:53 | 45694.1618 | 2025-02-06 06:38 | 45694.2764 | 0.1216 | 0.00073694 | 25 | 4125 | Unplanned | Unknown | Unknown
1295 |  | WMR163 | ABS W117 |  | Waikakahi | 2025-02-06 03:53 | 45694.1618 | 2025-02-06 06:58 | 45694.2903 | 1.0143 | 0.0054828 | 186 | 34410 | Unplanned | Unknown | Unknown
1296 |  | WMR164/165 | Links T785 @ Pole #03968 |  | Waitohi | 2025-02-06 23:53 | 45694.9951 | 2025-02-07 03:00 | 45695.125 | 0.038586 | 0.00020634 | 7 | 1309 | Unplanned | Third party interference | Car v Pole
1297 |  | WMR164/165 | TMK CB9 -(ABS T315 - Links T785 @ Pole #03968) |  | Waitohi | 2025-02-06 23:53 | 45694.9951 | 2025-02-07 05:31 | 45695.2299 | 2.1621 | 0.0063967 | 217 | 73346 | Unplanned | Third party interference | Car v Pole
1298 |  | WMR164/165 | ABS T315 - Links T785 @ Pole #03968 |  | Waitohi | 2025-02-06 23:53 | 45694.9951 | 2025-02-07 08:26 | 45695.3514 | 1.1039 | 0.0021519 | 73 | 37449 | Unplanned | Third party interference | Car v Pole
1299 |  | WMR164/165 | Links T785 @ Pole #03968 |  | Waitohi | 2025-02-07 08:16 | 45695.3444 | 2025-02-07 08:26 | 45695.3514 | 0.0020634 | 0.00020634 | 7 | 70 | Unplanned | Third party interference | Car v Pole
1300 |  | 4653 | Fuses TOB1463 |  | Normanby | 2025-02-07 12:04 | 45695.5028 | 2025-02-07 13:39 | 45695.5687 | 0.0084011 | 8.8433e-05 | 3 | 285 | Unplanned | Third party interference | Damaged Stay wire
1301 |  | 1210 | Fuses TOB1463 |  | Normanby | 2025-02-07 12:04 | 45695.5028 | 2025-02-07 13:39 | 45695.5687 | 0.0084011 | 8.8433e-05 | 3 | 285 | Unplanned | Third party interference | Blown Fuses due to stay wire in contact with lines
1302 |  | WMR166 | STU CB9 - Links W742 |  | Morven | 2025-02-09 02:39 | 45697.1104 | 2025-02-09 04:56 | 45697.2056 | 1.3811 | 0.010081 | 342 | 46854 | Unplanned | Wildlife | Bird strike
1303 |  | WMR166 | Links W742 |  | Morven | 2025-02-09 02:39 | 45697.1104 | 2025-02-09 08:02 | 45697.3347 | 0.12378 | 0.00038321 | 13 | 4199 | Unplanned | Wildlife | Bird strike
1304 |  | WMR167 | W590 - W494 |  | Tawai | 2025-02-09 06:14 | 45697.2597 | 2025-02-09 06:54 | 45697.2875 | 0.20163 | 0.0050407 | 171 | 6840 | Unplanned | Unknown | Unknown
1305 |  | WMR167 | W494 |  | Tawai | 2025-02-09 06:14 | 45697.2597 | 2025-02-09 07:36 | 45697.3167 | 0.22238 | 0.0027119 | 92 | 7544 | Unplanned | Unknown | Unknown
1306 |  | 1205 | Fuses L124-TX B100 |  | Holme Station | 2025-02-10 08:05 | 45698.3368 | 2025-02-10 08:38 | 45698.3597 | 0.0038911 | 0.00011791 | 4 | 132 | Unplanned | Vegetation | Bark on line
1307 |  | 1205 | TX B100 |  | Holme Station | 2025-02-10 08:05 | 45698.3368 | 2025-02-10 08:53 | 45698.3701 | 0.0014149 | 2.9478e-05 | 1 | 48 | Unplanned | Vegetation | Bark on line
1308 |  | GWM1245 | Links F453 to end |  | Totara Valley | 2025-02-10 09:00 | 45698.375 | 2025-02-10 13:49 | 45698.5757 | 0.15334 | 0.0005306 | 18 | 5202 | Planned | Planned interruption | Tree Cutting
1309 |  | SRT293 | W203 minus W710 minus W267 minus TX A544 |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 16:48 | 45699.7 | 0.031069 | 5.8955e-05 | 2 | 1054 | Planned | Planned interruption | TX Upgrade
1310 |  | SRT293 | TX A544 CCT2 minus #18 & #26 Leanord St |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:00 | 45699.7083 | 0.22244 | 0.00041269 | 14 | 7546 | Planned | Planned interruption | TX Upgrade
1311 |  | SRT293 | 18 Leonard St |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:05 | 45699.7118 | 0.016036 | 2.9478e-05 | 1 | 544 | Planned | Planned interruption | TX Upgrade
1312 |  | SRT293 | 26 Leonard St |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:06 | 45699.7125 | 0.016065 | 2.9478e-05 | 1 | 545 | Planned | Planned interruption | TX Upgrade
1313 |  | SRT293 | TX A544 CCT3 minus 156 High St and poles #22273/22274 |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:07 | 45699.7132 | 0.69208 | 0.0012675 | 43 | 23478 | Planned | Planned interruption | TX Upgrade
1314 |  | SRT293 | #156 High St |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:15 | 45699.7188 | 0.016331 | 2.9478e-05 | 1 | 554 | Planned | Planned interruption | TX Upgrade
1315 |  | SRT293 | ICP's fed from poles #22273/22274 |  | Waimate | 2025-02-11 08:01 | 45699.334 | 2025-02-11 17:16 | 45699.7194 | 0.06544 | 0.00011791 | 4 | 2220 | Planned | Planned interruption | TX Upgrade
1316 |  | JRM053 | TX E253 to end |  | Haldon-Lilybank | 2025-02-11 09:00 | 45699.375 | 2025-02-11 14:41 | 45699.6118 | 0.23119 | 0.00067799 | 23 | 7843 | Planned | Planned interruption | LB Replacement
1317 |  | JRM053 | TX E245 to end |  | Haldon-Lilybank | 2025-02-11 09:00 | 45699.375 | 2025-02-11 14:46 | 45699.6153 | 0.33658 | 0.00097276 | 33 | 11418 | Planned | Planned interruption | LB Replacement
1318 |  | JRM053 | TX E314 to end |  | Haldon-Lilybank | 2025-02-11 09:00 | 45699.375 | 2025-02-11 14:52 | 45699.6194 | 0.29053 | 0.00082537 | 28 | 9856 | Planned | Planned interruption | LB Replacement
1319 |  | JMR760 | RMU M146 FS to end |  | Lakeside Drive | 2025-02-11 11:51 | 45699.4938 | 2025-02-11 12:44 | 45699.5306 | 0.0062493 | 0.00011791 | 4 | 212 | Unplanned | Defective equipment | Repairs to LV bushing after flashover
1320 |  | ACD182 | W461 to end |  | Morven | 2025-02-12 08:30 | 45700.3542 | 2025-02-12 15:31 | 45700.6465 | 0.01241 | 2.9478e-05 | 1 | 421 | Planned | Planned interruption | Line Alteration (Delta Arms)
1321 |  | ACD182 | Links W742 minus W461, TX A233, A1154, A1157 & A1158 |  | Morven | 2025-02-12 08:31 | 45700.3549 | 2025-02-12 15:27 | 45700.6438 | 0.073576 | 0.00017687 | 6 | 2496 | Planned | Planned interruption | Line Alteration (Delta Arms)
1322 |  | ACD182 | TX A233 |  | Morven | 2025-02-12 08:31 | 45700.3549 | 2025-02-12 15:37 | 45700.6507 | 0.037672 | 8.8433e-05 | 3 | 1278 | Planned | Planned interruption | Line Alteration (Delta Arms)
1323 |  | ACD182 | TX A1154 |  | Morven | 2025-02-12 08:31 | 45700.3549 | 2025-02-12 15:43 | 45700.6549 | 0.012734 | 2.9478e-05 | 1 | 432 | Planned | Planned interruption | Line Alteration (Delta Arms)
1324 |  | ACD182 | TX A1157 |  | Morven | 2025-02-12 08:31 | 45700.3549 | 2025-02-12 15:48 | 45700.6583 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Line Alteration (Delta Arms)
1325 |  | ACD182 | TX A1158 |  | Morven | 2025-02-12 08:31 | 45700.3549 | 2025-02-12 15:55 | 45700.6632 | 0.013088 | 2.9478e-05 | 1 | 444 | Planned | Planned interruption | Line Alteration (Delta Arms)
1326 |  | ACD183 | W461 to end |  | Morven | 2025-02-13 08:30 | 45701.3542 | 2025-02-13 15:09 | 45701.6312 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Line Alteration (Delta Arms)
1327 |  | ACD183 | Links W742 minus W461, TX A856 |  | Morven | 2025-02-13 08:32 | 45701.3556 | 2025-02-13 15:05 | 45701.6285 | 0.12743 | 0.00032425 | 11 | 4323 | Planned | Planned interruption | Line Alteration (Delta Arms)
1328 |  | ACD183 | A856 to end |  | Morven | 2025-02-13 08:32 | 45701.3556 | 2025-02-13 15:18 | 45701.6375 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Line Alteration (Delta Arms)
1329 |  | 4753 | Fuses T317 to end |  | Waitohi | 2025-02-13 14:42 | 45701.6125 | 2025-02-13 18:30 | 45701.7708 | 0.12098 | 0.0005306 | 18 | 4104 | Unplanned | Third party interference | Mower vs pole #01317
1330 |  | 5026 | TVS CB3 Pukaki |  | Pukaki | 2025-02-14 09:00 | 45702.375 | 2025-02-14 11:03 | 45702.4604 | 0.15953 | 0.001297 | 44 | 5412 | Unplanned | Defective equipment | Broken insulator replacement
1331 |  | WMR168 | TX A1106 to end |  | Tawai | 2025-02-14 12:26 | 45702.5181 | 2025-02-14 12:31 | 45702.5215 | 0.00014739 | 2.9478e-05 | 1 | 5 | Planned | Planned interruption | TX Tap Change
1332 |  | SRS037 | TX B2116 to end |  | Washdyke | 2025-02-15 07:30 | 45703.3125 | 2025-02-15 13:16 | 45703.5528 | 0.010199 | 2.9478e-05 | 1 | 346 | Planned | Planned interruption | RMU Upgrade. DB Switched off for automation supply connection
1333 |  | GWM1244 | ABS W221 to end |  | Mt Studholme | 2025-02-15 09:00 | 45703.375 | 2025-02-15 12:00 | 45703.5 | 0.15918 | 0.00088433 | 30 | 5400 | Planned | Planned interruption | Tree Cutting
1334 |  | GWM1247 | Fuses W741 to end |  | Waihuna | 2025-02-17 09:20 | 45705.3889 | 2025-02-17 15:51 | 45705.6604 | 0.08068 | 0.00020634 | 7 | 2737 | Planned | Planned interruption | Tree Cutting
1335 |  | SRS032 | ICP fed from LB H360/5 |  | Stafford Street | 2025-02-17 18:47 | 45705.7826 | 2025-02-18 01:09 | 45706.0479 | 0.01126 | 2.9478e-05 | 1 | 382 | Planned | Planned interruption | Lucy Box Replacement
1336 |  | SRS032 | ICP fed from LB H360/6 |  | Stafford Street | 2025-02-17 18:47 | 45705.7826 | 2025-02-18 09:48 | 45706.4083 | 0.053119 | 5.8955e-05 | 2 | 1802 | Planned | Planned interruption | Lucy Box Replacement
1337 |  | SRS032 | ICP fed from LB H360/7 |  | Stafford Street | 2025-02-17 18:47 | 45705.7826 | 2025-02-18 08:33 | 45706.3562 | 0.073046 | 8.8433e-05 | 3 | 2478 | Planned | Planned interruption | Lucy Box Replacement
1338 |  | SRS032 | ICP fed from LB H360/8 |  | Stafford Street | 2025-02-17 18:47 | 45705.7826 | 2025-02-18 07:38 | 45706.3181 | 0.022727 | 2.9478e-05 | 1 | 771 | Planned | Planned interruption | Lucy Box Replacement
1339 |  | SRS032 | ICP fed from LB H360/4 |  | Stafford Street | 2025-02-17 18:47 | 45705.7826 | 2025-02-18 07:20 | 45706.3056 | 0.022197 | 2.9478e-05 | 1 | 753 | Planned | Planned interruption | Lucy Box Replacement
1340 |  | SRS032 | TE5 CCT19 |  | Stafford Street | 2025-02-17 19:00 | 45705.7917 | 2025-02-17 19:05 | 45705.7951 | 0.00058955 | 0.00011791 | 4 | 20 | Planned | Planned interruption | Lucy Box Replacement
1341 |  | SRS032 | TE5 CCT14 & TE5 CCT13 minus LB H289 CCT7 |  | Stafford Street | 2025-02-17 19:00 | 45705.7917 | 2025-02-17 19:06 | 45705.7958 | 0.0005306 | 8.8433e-05 | 3 | 18 | Planned | Planned interruption | Lucy Box Replacement
1342 |  | SRS032 | TE5 CCT14 & TE5 CCT13 minus LB H289 CCT7 |  | Stafford Street | 2025-02-18 00:50 | 45706.0347 | 2025-02-18 00:58 | 45706.0403 | 0.00070746 | 8.8433e-05 | 3 | 24 | Planned | Planned interruption | Lucy Box Replacement
1343 |  | SRS032 | TE5 CCT19 |  | Stafford Street | 2025-02-18 00:52 | 45706.0361 | 2025-02-18 00:58 | 45706.0403 | 0.00070746 | 0.00011791 | 4 | 24 | Planned | Planned interruption | Lucy Box Replacement
1344 |  | 1206 | Fuses F331 to end |  | Fairlie Rural | 2025-02-18 15:40 | 45706.6528 | 2025-02-18 16:05 | 45706.6701 | 0.0044216 | 0.00017687 | 6 | 150 | Unplanned | Unknown | Blown Fuse
1345 |  | SRS033 | TE36 minus CCT13, CCT16 & Lucy box H6/3 |  | Stafford Street | 2025-02-18 18:27 | 45706.7688 | 2025-02-18 22:59 | 45706.9576 | 0.024054 | 8.8433e-05 | 3 | 816 | Planned | Planned interruption | Lucy Box Replacement
1346 |  | SKE1927 / SKE1931 | CB L107 to end minus Links L225 |  | Totara Valley | 2025-02-19 09:00 | 45707.375 | 2025-02-19 16:22 | 45707.6819 | 1.2378 | 0.0028004 | 95 | 41990 | Planned | Planned interruption | ABS Upgrade to LBS
1347 |  | SKE1927 / SKE1931 | Links L225 to end |  | Totara Valley | 2025-02-19 09:00 | 45707.375 | 2025-02-19 09:06 | 45707.3792 | 0.010966 | 0.0018276 | 62 | 372 | Planned | Planned interruption | ABS Upgrade to LBS
1348 |  | JRM057 | TX B1244 to end |  | Normanby | 2025-02-19 09:13 | 45707.384 | 2025-02-19 14:06 | 45707.5875 | 0.017274 | 5.8955e-05 | 2 | 586 | Planned | Planned interruption | TX Maintenance
1349 |  | 5134 | GLD CB G191 to Links G237 minus TX D1094 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:05 | 45707.5868 | 4.216 | 0.037643 | 1277 | 143024 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1350 |  | 5134 | RMU G232 to end |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:14 | 45707.5931 | 0.56712 | 0.0046869 | 159 | 19239 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1351 |  | 5134 | TX D854 Minus CCT2, CCT3, CCt4 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:40 | 45707.6111 | 0.0043332 | 2.9478e-05 | 1 | 147 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1352 |  | 5134 | TX D854 CCT2 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:41 | 45707.6118 | 0.043627 | 0.00029478 | 10 | 1480 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1353 |  | 5134 | TX D854 CCT3 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:32 | 45707.6056 | 0.049169 | 0.00035373 | 12 | 1668 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1354 |  | 5134 | TX D854 CCT4 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:30 | 45707.6042 | 0.096923 | 0.00070746 | 24 | 3288 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1355 |  | 5134 | TX D1094 Minus CCT2, CCT3 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:34 | 45707.6069 | 0.12469 | 0.00088433 | 30 | 4230 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1356 |  | 5134 | TX D1094 CCT2 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:26 | 45707.6014 | 0.019603 | 0.00014739 | 5 | 665 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1357 |  | 5134 | TX D1094 CCT3 |  | Geraldine Township | 2025-02-19 12:13 | 45707.509 | 2025-02-19 14:30 | 45707.6042 | 0.032308 | 0.00023582 | 8 | 1096 | Unplanned | Defective equipment | Cable Fault at RMU G240 Cable Box
1358 |  | 4756 | Fuses L122 |  | Holme Station | 2025-02-19 18:48 | 45707.7833 | 2025-02-19 20:33 | 45707.8562 | 0.046427 | 0.00044216 | 15 | 1575 | Unplanned | Lighting | Blown fuses due to lightning
1359 |  | 4756 | Fuses TOB538 |  | Holme Station | 2025-02-19 18:48 | 45707.7833 | 2025-02-19 20:30 | 45707.8542 | 0.0030067 | 2.9478e-05 | 1 | 102 | Unplanned | Lighting | Blown fuses due to lightning
1360 |  | 4755 | Fuses TOA869 |  | Mt Studholme | 2025-02-19 18:55 | 45707.7882 | 2025-02-19 20:07 | 45707.8382 | 0.0021224 | 2.9478e-05 | 1 | 72 | Unplanned | Lighting | Lightning
1361 |  | 4759 | Fuses TOA386 |  | Waikakahi | 2025-02-19 19:02 | 45707.7931 | 2025-02-20 10:09 | 45708.4229 | 0.026736 | 2.9478e-05 | 1 | 907 | Unplanned | Lighting | Blown fuses due to lightning
1362 |  | 4759 | Fuses TOA385 |  | Waikakahi | 2025-02-19 19:02 | 45707.7931 | 2025-02-20 10:05 | 45708.4201 | 0.026618 | 2.9478e-05 | 1 | 903 | Unplanned | Lighting | Blown fuses due to lightning
1363 |  | 4759 | Fuses TO809 |  | Waikakahi | 2025-02-19 19:02 | 45707.7931 | 2025-02-20 10:09 | 45708.4229 | 0.026736 | 2.9478e-05 | 1 | 907 | Unplanned | Lighting | Blown fuses due to lightning
1364 |  | 4759 | Fuses W538 |  | Waikakahi | 2025-02-19 19:02 | 45707.7931 | 2025-02-20 09:46 | 45708.4069 | 0.026058 | 2.9478e-05 | 1 | 884 | Unplanned | Lighting | Blown fuses due to lightning
1365 |  | 4761 | Fuses TOA384 |  | Waikakahi | 2025-02-19 19:02 | 45707.7931 | 2025-02-20 10:22 | 45708.4319 | 0.027119 | 2.9478e-05 | 1 | 920 | Unplanned | Lighting | Blown fuses due to lightning
1366 |  | 4754 | CB W196 to end |  | Morven | 2025-02-19 19:17 | 45707.8035 | 2025-02-19 20:35 | 45707.8576 | 0.10577 | 0.001356 | 46 | 3588 | Unplanned | Lighting | Lightning
1367 |  | 3916 | CB F426 - Links F107 - Fuses TOC32 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 10:17 | 45708.4285 | 0.51937 | 0.00061903 | 21 | 17619 | Unplanned | Lighting | Lightning
1368 |  | 3916 | Links F107 - Fuses F110 - Fuses F109 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 11:30 | 45708.4792 | 0.18819 | 0.00020634 | 7 | 6384 | Unplanned | Lighting | Lightning
1369 |  | 3916 | Fuses F109 to end |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 11:35 | 45708.4826 | 0.081093 | 8.8433e-05 | 3 | 2751 | Unplanned | Lighting | Lightning
1370 |  | 3916 | Fuses F110 - Fuses F111 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 12:02 | 45708.5014 | 0.3061 | 0.00032425 | 11 | 10384 | Unplanned | Lighting | Lightning
1371 |  | 3916 | Fuses F111 - Fuses F105 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 12:48 | 45708.5333 | 0.029183 | 2.9478e-05 | 1 | 990 | Unplanned | Lighting | Lightning
1372 |  | 3916 | Fuses F105 to end |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 13:17 | 45708.5535 | 0.15019 | 0.00014739 | 5 | 5095 | Unplanned | Lighting | Lightning
1373 |  | 3918 | Fuses TOC32 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 15:10 | 45708.6319 | 0.033369 | 2.9478e-05 | 1 | 1132 | Unplanned | Lighting | Lightning
1374 |  | 4761 | Fuses TOC353 |  | Cave | 2025-02-19 20:18 | 45707.8458 | 2025-02-20 08:46 | 45708.3653 | 0.022049 | 2.9478e-05 | 1 | 748 | Unplanned | Lighting | Blown fuses due to lightning
1375 |  | 4759 | Fuses TOA855 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 09:10 | 45708.3819 | 0.044924 | 5.8955e-05 | 2 | 1524 | Unplanned | Lighting | Blown fuses due to lightning
1376 |  | 4759 | Fuses TOA1422 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 09:10 | 45708.3819 | 0.022462 | 2.9478e-05 | 1 | 762 | Unplanned | Lighting | Blown fuses due to lightning
1377 |  | 4759 | Fuses TOA8 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 08:30 | 45708.3542 | 0.021283 | 2.9478e-05 | 1 | 722 | Unplanned | Lighting | Blown fuses due to lightning
1378 |  | 4759 | Fuses TOA7 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 09:26 | 45708.3931 | 0.068801 | 8.8433e-05 | 3 | 2334 | Unplanned | Lighting | Blown fuses due to lightning
1379 |  | 4759 | Fuses TOA6 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 09:00 | 45708.375 | 0.044334 | 5.8955e-05 | 2 | 1504 | Unplanned | Lighting | Blown fuses due to lightning
1380 |  | 4759 | Fuses TOA1548 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 08:45 | 45708.3646 | 0.021725 | 2.9478e-05 | 1 | 737 | Unplanned | Lighting | Blown fuses due to lightning
1381 |  | 4760 | Fuses TOA1291 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 13:50 | 45708.5764 | 0.030716 | 2.9478e-05 | 1 | 1042 | Unplanned | Lighting | Blown Tx due to lightning
1382 |  | 4761 | Fuses TOA10 |  | St Andrews | 2025-02-19 20:28 | 45707.8528 | 2025-02-20 12:48 | 45708.5333 | 0.057776 | 5.8955e-05 | 2 | 1960 | Unplanned | Lighting | Blown fuses due to lightning
1383 |  | 4761 | Fuses TOB1322 |  | St Andrews | 2025-02-19 20:31 | 45707.8549 | 2025-02-20 09:45 | 45708.4062 | 0.023405 | 2.9478e-05 | 1 | 794 | Unplanned | Lighting | Blown fuses due to lightning
1384 |  | 4757 | CB W664 - ABS W258 |  | Waihaorunga | 2025-02-19 23:05 | 45707.9618 | 2025-02-19 23:39 | 45707.9854 | 0.449 | 0.013206 | 448 | 15232 | Unplanned | Defective equipment | Broken insulator pole #20685
1385 |  | 4757 | ABS W258 - ABS W254 |  | Waihaorunga | 2025-02-19 23:05 | 45707.9618 | 2025-02-19 23:52 | 45707.9944 | 0.48906 | 0.010406 | 353 | 16591 | Unplanned | Defective equipment | Broken insulator pole #20685
1386 |  | 4757 | CB W664 - ABS W263 |  | Waihaorunga | 2025-02-19 23:40 | 45707.9861 | 2025-02-19 23:45 | 45707.9896 | 0.022698 | 0.0045396 | 154 | 770 | Unplanned | Defective equipment | Broken insulator pole #20685
1387 |  | 4757 | ABS W263 - ABS W258 |  | Waihaorunga | 2025-02-19 23:40 | 45707.9861 | 2025-02-20 02:49 | 45708.1174 | 1.638 | 0.0086664 | 294 | 55566 | Unplanned | Defective equipment | Broken insulator pole #20685
1388 |  | SKE1932 | ABS L109 (new LBS L1496) to end minus links L225 |  | Totara Valley | 2025-02-20 09:00 | 45708.375 | 2025-02-20 10:54 | 45708.4542 | 0.11089 | 0.00097276 | 33 | 3762 | Planned | Planned interruption | LBS commissioning
1389 |  | 3916 | CB F426 - Links F107 - Fuses TOC32 |  | Cave | 2025-02-20 11:26 | 45708.4764 | 2025-02-20 11:30 | 45708.4792 | 0.0024761 | 0.00061903 | 21 | 84 | Unplanned | Lighting | Lightning
1390 |  | 4760 | CB W598 - ABS W417 |  | St Andrews | 2025-02-20 12:00 | 45708.5 | 2025-02-20 13:32 | 45708.5639 | 0.13017 | 0.0014149 | 48 | 4416 | Unplanned | Lighting | Blown Tx due to lightning
1391 |  | 3918 | Fuses F103 - Fuses TOC32 |  | Cave | 2025-02-20 12:45 | 45708.5312 | 2025-02-20 14:45 | 45708.6146 | 0.024761 | 0.00020634 | 7 | 840 | Unplanned | Lighting | Lightning
1392 |  | 5028 | G328 to end |  | Geraldine Township | 2025-02-21 07:30 | 45709.3125 | 2025-02-21 12:19 | 45709.5132 | 0.11927 | 0.00041269 | 14 | 4046 | Unplanned | Vegetation | Trees on line @ P#50789 - P#35022
1393 |  | 4758 | Fuses TOA48 |  | St Andrews | 2025-02-21 08:46 | 45709.3653 | 2025-02-24 12:37 | 45712.5257 | 0.26831 | 5.8955e-05 | 2 | 9102 | Unplanned | Defective equipment | Blown Tx A48 due to Lightning storm
1394 |  | JDJ158 | CB W470 to Links at pole #28974 & ABS W337 minus TX A1 |  | St Andrews | 2025-02-21 08:47 | 45709.366 | 2025-02-21 12:32 | 45709.5222 | 0.099487 | 0.00044216 | 15 | 3375 | Planned | Planned interruption | Lines maintenance
1395 |  | JDJ158 | TX A1 to end |  | St Andrews | 2025-02-21 08:47 | 45709.366 | 2025-02-21 13:18 | 45709.5542 | 0.015977 | 5.8955e-05 | 2 | 542 | Planned | Planned interruption | Lines maintenance
1396 |  | JDJ158 | ABS W337 to CB W598 |  | St Andrews | 2025-02-21 08:47 | 45709.366 | 2025-02-21 12:43 | 45709.5299 | 0.59828 | 0.0025351 | 86 | 20296 | Planned | Planned interruption | Lines maintenance
1397 |  | JDJ158 | ABS W648 to end |  | St Andrews | 2025-02-21 08:47 | 45709.366 | 2025-02-21 12:49 | 45709.534 | 0.16407 | 0.00067799 | 23 | 5566 | Planned | Planned interruption | Lines maintenance
1398 |  | JDJ158 | Temp Links at pole #28974 to end + CB W598 to end minus ABS W598 |  | St Andrews | 2025-02-21 08:47 | 45709.366 | 2025-02-21 08:58 | 45709.3736 | 0.018158 | 0.0016507 | 56 | 616 | Planned | Planned interruption | Lines maintenance
1399 |  | JDJ158 | Regs A1228 to CB W470 |  | St Andrews | 2025-02-21 09:10 | 45709.3819 | 2025-02-21 12:15 | 45709.5104 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Lines maintenance
1400 |  | JDJ158 | Temp Links at pole #28974 to end + CB W598 to end minus ABS W598 |  | St Andrews | 2025-02-21 12:23 | 45709.516 | 2025-02-21 12:32 | 45709.5222 | 0.014857 | 0.0016507 | 56 | 504 | Planned | Planned interruption | Lines maintenance
1401 |  | 5135 | G165 to end minus TX D292 |  | Woodbury | 2025-02-21 14:29 | 45709.6035 | 2025-02-21 16:40 | 45709.6944 | 0.0077231 | 5.8955e-05 | 2 | 262 | Unplanned | Unknown | Unknown
1402 |  | 5135 | TX D292 to end |  | Woodbury | 2025-02-21 14:29 | 45709.6035 | 2025-02-21 16:50 | 45709.7014 | 0.0041563 | 2.9478e-05 | 1 | 141 | Unplanned | Unknown | Unknown
1403 |  | SRS035A & B | RMU L1264 minus CB L876 Minus RMU L1140 minus TX B1959, TX B1245 minus Fuses L192 |  | Levels Plain | 2025-02-22 06:35 | 45710.2743 | 2025-02-22 15:36 | 45710.65 | 0.079737 | 0.00014739 | 5 | 2705 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1404 |  | SRS035A & B | Fuses L192 minus TX B264 |  | Levels Plain | 2025-02-22 06:35 | 45710.2743 | 2025-02-22 17:04 | 45710.7111 | 0.018541 | 2.9478e-05 | 1 | 629 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1405 |  | SRS035A & B | TX B264 |  | Levels Plain | 2025-02-22 06:35 | 45710.2743 | 2025-02-22 13:12 | 45710.55 | 0.023405 | 5.8955e-05 | 2 | 794 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1406 |  | SRS035A & B | RMU L780 to CB L355 (Links L356) |  | Arowhenua | 2025-02-22 06:35 | 45710.2743 | 2025-02-22 15:26 | 45710.6431 | 0.26609 | 0.00050112 | 17 | 9027 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1407 |  | SRS035A & B | CB L876 minus Links L1253 |  | Levels Plain | 2025-02-22 06:36 | 45710.275 | 2025-02-22 15:48 | 45710.6583 | 0.30916 | 0.00056008 | 19 | 10488 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1408 |  | SRS035A & B | TX B264 |  | Levels Plain | 2025-02-22 16:39 | 45710.6937 | 2025-02-22 17:04 | 45710.7111 | 0.0014739 | 5.8955e-05 | 2 | 50 | Planned | Planned interruption | RMU & Field Recloser replacements / Upgrades
1409 |  | SRT295 | Links L225 - ABS FX16 |  | Totara Valley | 2025-02-24 09:00 | 45712.375 | 2025-02-24 09:06 | 45712.3792 | 0.0035373 | 0.00058955 | 20 | 120 | Planned | Planned interruption | Replace LB ABS LX92
1410 |  | 4758 | ABS W324 - ABS W457 |  | St Andrews | 2025-02-24 11:14 | 45712.4681 | 2025-02-24 12:16 | 45712.5111 | 0.023759 | 0.00038321 | 13 | 806 | Unplanned | Defective equipment | Blown Tx A48 due to Lightning storm
1411 |  | SRT295 | ABS FX16 - LB ABS F122 |  | Totara Valley | 2025-02-24 16:00 | 45712.6667 | 2025-02-24 16:02 | 45712.6681 | 0.0024761 | 0.0012381 | 42 | 84 | Planned | Planned interruption | Replace LB ABS LX92
1412 |  | JDJ159 | ABS W337 - CB W598 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 16:53 | 45713.7035 | 1.2371 | 0.0025351 | 86 | 41968 | Planned | Planned interruption | Lines Maintenance
1413 |  | JDJ159 | W470 - p#28974 - ABS W337 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 16:38 | 45713.6931 | 0.13943 | 0.00029478 | 10 | 4730 | Planned | Planned interruption | Lines Maintenance
1414 |  | JDJ159 | W598 + p#28974 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 09:01 | 45713.3757 | 0.026412 | 0.0016507 | 56 | 896 | Planned | Planned interruption | Lines Maintenance
1415 |  | JDJ159 | W648 to end |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 17:27 | 45713.7271 | 0.35391 | 0.00067799 | 23 | 12006 | Planned | Planned interruption | Lines Maintenance
1416 |  | JDJ159 | Tx A45 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 18:16 | 45713.7611 | 0.016832 | 2.9478e-05 | 1 | 571 | Planned | Planned interruption | Lines Maintenance
1417 |  | JDJ159 | Tx A1 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 17:43 | 45713.7382 | 0.031718 | 5.8955e-05 | 2 | 1076 | Planned | Planned interruption | Lines Maintenance
1418 |  | JDJ159 | Tx A1343 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 17:58 | 45713.7486 | 0.016301 | 2.9478e-05 | 1 | 553 | Planned | Planned interruption | Lines Maintenance
1419 |  | JDJ159 | Tx A757 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 18:10 | 45713.7569 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Lines Maintenance
1420 |  | JDJ159 | Tx A733 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 18:28 | 45713.7694 | 0.017185 | 2.9478e-05 | 1 | 583 | Planned | Planned interruption | Lines Maintenance
1421 |  | JDJ159 | Tx A732 |  | St Andrews | 2025-02-25 08:45 | 45713.3646 | 2025-02-25 18:17 | 45713.7618 | 0.016861 | 2.9478e-05 | 1 | 572 | Planned | Planned interruption | Lines Maintenance
1422 |  | SKE1928 | Old ABS L221 (N LBS L1510) |  | Totara Valley | 2025-02-25 09:00 | 45713.375 | 2025-02-25 11:00 | 45713.4583 | 0.18748 | 0.0015623 | 53 | 6360 | Planned | Planned interruption | LBS commissioning
1423 |  | JDJ159 | L294 - W470 |  | St Andrews | 2025-02-25 09:11 | 45713.3826 | 2025-02-25 16:28 | 45713.6861 | 0.012882 | 2.9478e-05 | 1 | 437 | Planned | Planned interruption | Lines Maintenance
1424 |  | JDJ159 | W598 + p#28974 |  | St Andrews | 2025-02-25 16:30 | 45713.6875 | 2025-02-25 16:38 | 45713.6931 | 0.013206 | 0.0016507 | 56 | 448 | Planned | Planned interruption | Lines Maintenance
1425 |  | JDJ159/4762 | CB W470 minus ABS W648 |  | St Andrews | 2025-02-25 16:53 | 45713.7035 | 2025-02-25 17:19 | 45713.7215 | 0.12186 | 0.0046869 | 159 | 4134 | Unplanned | Defective equipment | Faulty Link p#28974
1426 |  | JDJ161 | Fuses W331 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:02 | 45714.7097 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Lines maintenance
1427 |  | JDJ161 | Tx A549 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:16 | 45714.7194 | 0.015093 | 2.9478e-05 | 1 | 512 | Planned | Planned interruption | Lines maintenance
1428 |  | JDJ161 | Tx A732 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:30 | 45714.7292 | 0.015505 | 2.9478e-05 | 1 | 526 | Planned | Planned interruption | Lines maintenance
1429 |  | JDJ161 | LV to 113 Otaio River Rd |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:34 | 45714.7319 | 0.015623 | 2.9478e-05 | 1 | 530 | Planned | Planned interruption | Lines maintenance
1430 |  | JDJ161 | LV to 129 Otaio River Rd |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:37 | 45714.734 | 0.015712 | 2.9478e-05 | 1 | 533 | Planned | Planned interruption | Lines maintenance
1431 |  | JDJ161 | Tx A757 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 17:55 | 45714.7465 | 0.016242 | 2.9478e-05 | 1 | 551 | Planned | Planned interruption | Lines maintenance
1432 |  | JDJ161 | Tx A733 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 18:09 | 45714.7562 | 0.016655 | 2.9478e-05 | 1 | 565 | Planned | Planned interruption | Lines maintenance
1433 |  | JDJ161 | Tx A3 |  | St Andrews | 2025-02-26 08:44 | 45714.3639 | 2025-02-26 18:23 | 45714.766 | 0.017068 | 2.9478e-05 | 1 | 579 | Planned | Planned interruption | Lines maintenance
1434 |  | JDJ160 | P#28974 - ABS W324 |  | St Andrews | 2025-02-26 08:45 | 45714.3646 | 2025-02-26 14:19 | 45714.5965 | 0.0098455 | 2.9478e-05 | 1 | 334 | Planned | Planned interruption | Lines Maintenance
1435 |  | JDJ152 | T780 - LB ABS WX48 |  | Woodbury | 2025-02-26 08:57 | 45714.3729 | 2025-02-26 09:00 | 45714.375 | 0.0002653 | 8.8433e-05 | 3 | 9 | Planned | Planned interruption | Lines maintenance
1436 |  | SRS039 | D1404-CCT2 + pool minus LG005 |  | Geraldine Township | 2025-02-26 09:12 | 45714.3833 | 2025-02-26 10:09 | 45714.4229 | 0.0084011 | 0.00014739 | 5 | 285 | Planned | Planned interruption | New equipment install TX D2148, Outage started and was then cancelled due to sensitive customer
1437 |  | JDJ152 | T780 - LB ABS WX48 |  | Woodbury | 2025-02-26 15:00 | 45714.625 | 2025-02-26 15:03 | 45714.6271 | 0.0002653 | 8.8433e-05 | 3 | 9 | Planned | Planned interruption | Lines maintenance
1438 |  | ACD185 | Fuses W460 |  | St Andrews | 2025-02-28 09:00 | 45716.375 | 2025-02-28 11:19 | 45716.4715 | 0.020487 | 0.00014739 | 5 | 695 | Planned | Planned interruption | Lines maintenance
1439 |  | GWM1254 | Fuses G272 |  | Speechley | 2025-02-28 09:00 | 45716.375 | 2025-02-28 13:30 | 45716.5625 | 0.031836 | 0.00011791 | 4 | 1080 | Planned | Planned interruption | Tree cutting
1440 |  | ACD186 | Tx B249 |  | Arowhenua | 2025-02-28 09:00 | 45716.375 | 2025-02-28 12:12 | 45716.5083 | 0.11319 | 0.00058955 | 20 | 3840 | Planned | Planned interruption | Tx B249 & B720 replacement
1441 |  | ACD186 | ABS L318 - ABS L319 |  | Arowhenua | 2025-02-28 09:00 | 45716.375 | 2025-02-28 12:29 | 45716.5201 | 0.56064 | 0.0026825 | 91 | 19019 | Planned | Planned interruption | Tx B249 & B720 replacement
1442 |  | 5454 | TX A1556 to end |  | Glenavy | 2025-02-28 13:13 | 45716.5507 | 2025-02-28 13:28 | 45716.5611 | 0.00044216 | 2.9478e-05 | 1 | 15 | Unplanned | Defective equipment | Tap Change
1443 |  | PJD1736 | TX D1006 |  | Speechley | 2025-03-01 10:15 | 45717.4271 | 2025-03-01 13:20 | 45717.5556 | 0.0054534 | 2.9478e-05 | 1 | 185 | Planned | Planned interruption | Replace LAs & Dos
1444 |  | SEM131 | STU CB2 (Glenavy) - Links W144 |  | Glenavy | 2025-03-01 10:38 | 45717.4431 | 2025-03-01 11:27 | 45717.4771 | 0.27155 | 0.0055418 | 188 | 9212 | Unplanned | Third party interference | Truck on fire near pole #817083
1445 |  | SEM131 | Links W144 to end |  | Glenavy | 2025-03-01 10:38 | 45717.4431 | 2025-03-01 13:11 | 45717.5493 | 0.02255 | 0.00014739 | 5 | 765 | Unplanned | Third party interference | Truck on fire near pole #817083
1446 |  | SEM132 | STU CB2 (Glenavy) - Links W144 |  | Glenavy | 2025-03-01 15:11 | 45717.6326 | 2025-03-01 15:47 | 45717.6576 | 0.1995 | 0.0055418 | 188 | 6768 | Unplanned | Third party interference | Hay fire near pole #817083
1447 |  | SEM132 | Links W144 to end |  | Glenavy | 2025-03-01 15:11 | 45717.6326 | 2025-03-01 16:47 | 45717.6993 | 0.014149 | 0.00014739 | 5 | 480 | Unplanned | Third party interference | Hay fire near pole #817083
1448 |  | SEM133 | Fuses TO C420 |  | Cricklewood | 2025-03-01 23:50 | 45717.9931 | 2025-03-02 00:45 | 45718.0312 | 0.0016213 | 2.9478e-05 | 1 | 55 | Unplanned | Defective equipment | Burnt LV Fuse carrier
1449 |  | 5455 | Links F209 to end |  | Cricklewood | 2025-03-03 09:06 | 45719.3792 | 2025-03-03 13:14 | 45719.5514 | 0.10235 | 0.00041269 | 14 | 3472 | Unplanned | Third party interference | Truck Vs Lines
1450 |  | JDJ168 | TX D664 |  | Woodbury | 2025-03-03 09:50 | 45719.4097 | 2025-03-03 11:49 | 45719.4924 | 0.0070157 | 5.8955e-05 | 2 | 238 | Planned | Planned interruption | Red tag pole replacement
1451 |  | JDJ163 | TX A733 |  | St Andrews | 2025-03-04 08:45 | 45720.3646 | 2025-03-04 17:08 | 45720.7139 | 0.014827 | 2.9478e-05 | 1 | 503 | Planned | Planned interruption | Otaio Line Maintenance
1452 |  | JDJ163 | Fuses W321-TX A733 |  | St Andrews | 2025-03-04 08:45 | 45720.3646 | 2025-03-04 16:54 | 45720.7042 | 0.014415 | 2.9478e-05 | 1 | 489 | Planned | Planned interruption | Otaio Line Maintenance
1453 |  | 5077 | Fuses TOA1422 |  | St Andrews | 2025-03-04 13:29 | 45720.5618 | 2025-03-04 17:31 | 45720.7299 | 0.0071336 | 2.9478e-05 | 1 | 242 | Unplanned | Defective equipment | TX A1422 Failed
1454 |  | 5077 | Fuses W326 |  | St Andrews | 2025-03-04 15:46 | 45720.6569 | 2025-03-04 17:16 | 45720.7194 | 0.034489 | 0.00038321 | 13 | 1170 | Unplanned | Defective equipment | TX A1422 Failed
1455 |  | ACD187 | CB G295-ABS G184 |  | Woodbury | 2025-03-05 09:04 | 45721.3778 | 2025-03-05 12:20 | 45721.5139 | 0.10977 | 0.00056008 | 19 | 3724 | Planned | Planned interruption | Red tag pole replacement
1456 |  | 5456 | BPD CB2 - ABS W554 |  | Tawai | 2025-03-06 05:40 | 45722.2361 | 2025-03-06 15:51 | 45722.6604 | 0.43226 | 0.00070746 | 24 | 14664 | Unplanned | Third party interference | Car v Pole #31151
1457 |  | 5456 | ABS W554 |  | Tawai | 2025-03-06 05:40 | 45722.2361 | 2025-03-06 07:13 | 45722.3007 | 0.87451 | 0.0094034 | 319 | 29667 | Unplanned | Third party interference | Car v Pole #31151
1458 |  | SRT285 | TX A72 |  | Otaio | 2025-03-06 08:30 | 45722.3542 | 2025-03-06 14:54 | 45722.6208 | 0.033958 | 8.8433e-05 | 3 | 1152 | Planned | Planned interruption | Makikihi Line Maintenance
1459 |  | SRT285 | Temp links Pole #29337-TX A72 |  | Otaio | 2025-03-06 08:30 | 45722.3542 | 2025-03-06 14:37 | 45722.609 | 0.010818 | 2.9478e-05 | 1 | 367 | Planned | Planned interruption | Makikihi Line Maintenance
1460 |  | 5456 | ABS W554 |  | Tawai | 2025-03-06 16:12 | 45722.675 | 2025-03-06 16:13 | 45722.6757 | 0.0094034 | 0.0094034 | 319 | 319 | Unplanned | Third party interference | Car v Pole #31151
1461 |  | 5456 | W176 |  | Tawai | 2025-03-06 16:12 | 45722.675 | 2025-03-06 16:13 | 45722.6757 | 0.00014739 | 0.00014739 | 5 | 5 | Unplanned | Third party interference | Car v Pole #31151
1462 |  | SRT290 & SKE1797 | CB W465 |  | Otaio | 2025-03-07 08:30 | 45723.3542 | 2025-03-07 15:59 | 45723.666 | 1.125 | 0.0025056 | 85 | 38165 | Planned | Planned interruption | Makikihi Line Maintenance
1463 |  | SRT290 & SKE1797 | CB W685-Temp Links Pole #43015 |  | Otaio | 2025-03-07 08:30 | 45723.3542 | 2025-03-07 16:44 | 45723.6972 | 0.043686 | 8.8433e-05 | 3 | 1482 | Planned | Planned interruption | Makikihi Line Maintenance
1464 |  | SRT290 & SKE1797 | Temp Links Pole #43015 |  | Otaio | 2025-03-07 08:30 | 45723.3542 | 2025-03-07 08:38 | 45723.3597 | 0.014149 | 0.0017687 | 60 | 480 | Planned | Planned interruption | Makikihi Line Maintenance
1465 |  | SRT290 & SKE1797 | ABS W302-ABS W303 |  | Otaio | 2025-03-07 08:30 | 45723.3542 | 2025-03-07 15:56 | 45723.6639 | 0.19721 | 0.00044216 | 15 | 6690 | Planned | Planned interruption | Makikihi Line Maintenance
1466 |  | SRT290 & SKE1797 | Pole #43083 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:12 | 45723.675 | 0.027178 | 5.8955e-05 | 2 | 922 | Planned | Planned interruption | Makikihi Line Maintenance
1467 |  | SRT290 & SKE1797 | Pole #43082 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:06 | 45723.6708 | 0.013412 | 2.9478e-05 | 1 | 455 | Planned | Planned interruption | Makikihi Line Maintenance
1468 |  | SRT290 & SKE1797 | Pole #43033 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:07 | 45723.6715 | 0.040325 | 8.8433e-05 | 3 | 1368 | Planned | Planned interruption | Makikihi Line Maintenance
1469 |  | SRT290 & SKE1797 | TX A683 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:26 | 45723.6847 | 0.014002 | 2.9478e-05 | 1 | 475 | Planned | Planned interruption | Makikihi Line Maintenance
1470 |  | SRT290 & SKE1797 | TX A895 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:27 | 45723.6854 | 0.028063 | 5.8955e-05 | 2 | 952 | Planned | Planned interruption | Makikihi Line Maintenance
1471 |  | SRT290 & SKE1797 | TX A88 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:24 | 45723.6833 | 0.041829 | 8.8433e-05 | 3 | 1419 | Planned | Planned interruption | Makikihi Line Maintenance
1472 |  | SRT290 & SKE1797 | TX A786 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:22 | 45723.6819 | 0.013884 | 2.9478e-05 | 1 | 471 | Planned | Planned interruption | Makikihi Line Maintenance
1473 |  | SRT290 & SKE1797 | TX A1421 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:20 | 45723.6806 | 0.013825 | 2.9478e-05 | 1 | 469 | Planned | Planned interruption | Makikihi Line Maintenance
1474 |  | SRT290 & SKE1797 | TX A87 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:13 | 45723.6757 | 0.068093 | 0.00014739 | 5 | 2310 | Planned | Planned interruption | Makikihi Line Maintenance
1475 |  | SRT290 & SKE1797 | Links W348-pole #43083-Pole #43082-Pole #43033-TX A683-TX A895-TX A88-TX A786-TX A1421-TX A87-CB W465-CB W685-TX A628 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 15:52 | 45723.6611 | 0.63698 | 0.0014444 | 49 | 21609 | Planned | Planned interruption | Makikihi Line Maintenance
1476 |  | SRT290 & SKE1797 | TX A628 |  | Otaio | 2025-03-07 08:31 | 45723.3549 | 2025-03-07 16:09 | 45723.6729 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Makikihi Line Maintenance
1477 |  | SRT290 & SKE1797 | Temp Links Pole #43015 |  | Otaio | 2025-03-07 16:40 | 45723.6944 | 2025-03-07 16:44 | 45723.6972 | 0.0070746 | 0.0017687 | 60 | 240 | Planned | Planned interruption | Makikihi Line Maintenance
1478 |  | GWM1257 | ABS T404 |  | Rangitata | 2025-03-10 09:00 | 45726.375 | 2025-03-10 15:42 | 45726.6542 | 0.15405 | 0.00038321 | 13 | 5226 | Planned | Planned interruption | Tree Cutting
1479 |  | SRT286 | Temp Links at pole #29337 to end |  | Otaio | 2025-03-11 08:33 | 45727.3562 | 2025-03-11 08:37 | 45727.359 | 0.00047164 | 0.00011791 | 4 | 16 | Planned | Planned interruption | Makikihi Line Maintenance
1480 |  | SRT286 | Temp Links at pole #43015 to pole #29337 minus TX A31 & TX A558 |  | Otaio | 2025-03-11 08:33 | 45727.3562 | 2025-03-11 15:35 | 45727.6493 | 0.6593 | 0.0015623 | 53 | 22366 | Planned | Planned interruption | Makikihi Line Maintenance
1481 |  | SRT286 | TX A31 to end |  | Otaio | 2025-03-11 08:33 | 45727.3562 | 2025-03-11 15:55 | 45727.6632 | 0.013029 | 2.9478e-05 | 1 | 442 | Planned | Planned interruption | Makikihi Line Maintenance
1482 |  | SRT286 | TX A558 to end |  | Otaio | 2025-03-11 08:33 | 45727.3562 | 2025-03-11 15:56 | 45727.6639 | 0.026117 | 5.8955e-05 | 2 | 886 | Planned | Planned interruption | Makikihi Line Maintenance
1483 |  | 5136 | TX D24 to end |  | Milford | 2025-03-11 18:38 | 45727.7764 | 2025-03-12 11:45 | 45728.4896 | 0.030274 | 2.9478e-05 | 1 | 1027 | Unplanned | Adverse weather | Broken Pole - Wind - Tree branch
1484 |  | SRT287 | Temp links at pole #43015 to pole #29337 minus TX's A1424, A1119, A1205, A75, A1248, A1258, LV Fuses at pole #29482, Links W362 and Fuses W344 |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:05 | 45728.6285 | 0.35456 | 0.00091381 | 31 | 12028 | Planned | Planned interruption | Makikihi Line Maintenance
1485 |  | SRT287 | A1424 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:23 | 45728.641 | 0.011968 | 2.9478e-05 | 1 | 406 | Planned | Planned interruption | Makikihi Line Maintenance
1486 |  | SRT287 | A1119 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:29 | 45728.6451 | 0.012145 | 2.9478e-05 | 1 | 412 | Planned | Planned interruption | Makikihi Line Maintenance
1487 |  | SRT287 | A1205 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:32 | 45728.6472 | 0.012233 | 2.9478e-05 | 1 | 415 | Planned | Planned interruption | Makikihi Line Maintenance
1488 |  | SRT287 | A75 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:24 | 45728.6417 | 0.059987 | 0.00014739 | 5 | 2035 | Planned | Planned interruption | Makikihi Line Maintenance
1489 |  | SRT287 | A1248 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:22 | 45728.6403 | 0.011938 | 2.9478e-05 | 1 | 405 | Planned | Planned interruption | Makikihi Line Maintenance
1490 |  | SRT287 | A1258 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:16 | 45728.6361 | 0.011762 | 2.9478e-05 | 1 | 399 | Planned | Planned interruption | Makikihi Line Maintenance
1491 |  | SRT287 | Fuses W362 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:28 | 45728.6444 | 0.048461 | 0.00011791 | 4 | 1644 | Planned | Planned interruption | Makikihi Line Maintenance
1492 |  | SRT287 | Links W344 to end |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:26 | 45728.6431 | 0.10851 | 0.0002653 | 9 | 3681 | Planned | Planned interruption | Makikihi Line Maintenance
1493 |  | SRT287 | LV Fuses at pole #29482 |  | Otaio | 2025-03-12 08:37 | 45728.359 | 2025-03-12 15:28 | 45728.6444 | 0.024231 | 5.8955e-05 | 2 | 822 | Planned | Planned interruption | Makikihi Line Maintenance
1494 |  | SRT287 | Temp Links at pole #29337 to end |  | Otaio | 2025-03-12 16:30 | 45728.6875 | 2025-03-12 16:33 | 45728.6896 | 0.00035373 | 0.00011791 | 4 | 12 | Planned | Planned interruption | Makikihi Line Maintenance
1495 |  | SRT289 | Fuses W340 to end |  | Otaio | 2025-03-13 08:30 | 45729.3542 | 2025-03-13 12:25 | 45729.5174 | 0.020782 | 8.8433e-05 | 3 | 705 | Planned | Planned interruption | Makikihi Line Maintenance
1496 |  | JDJ153 | TX D99 to end |  | Pleasant Point Township | 2025-03-14 09:06 | 45730.3792 | 2025-03-14 14:22 | 45730.5986 | 0.0093149 | 2.9478e-05 | 1 | 316 | Planned | Planned interruption | Lines Maintenance
1497 |  | SKE1919 | TE1 Minus LB J146/2, LB J146/4, LB J20, Council M/S (= DB J22) |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 18:22 | 45732.7653 | 0.060311 | 8.8433e-05 | 3 | 2046 | Planned | Planned interruption | Sub Maintenance
1498 |  | SKE1919 | Council M/S |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 18:01 | 45732.7507 | 0.019485 | 2.9478e-05 | 1 | 661 | Planned | Planned interruption | Sub Maintenance
1499 |  | SKE1919 | New LB H362/25 (= DB J98 - Old TE2 CCT22) |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 18:50 | 45732.7847 | 0.18836 | 0.0002653 | 9 | 6390 | Planned | Planned interruption | Sub Upgrade
1500 |  | SKE1919 | New LB H362/22 (= Telecom Exchange - Old TE2 CCT23) |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 18:59 | 45732.791 | 0.042389 | 5.8955e-05 | 2 | 1438 | Planned | Planned interruption | Sub Upgrade
1501 |  | SKE1919 | New LB H363/33 (St Mary's Church - Old TE2 CCT12) |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 19:03 | 45732.7937 | 0.021312 | 2.9478e-05 | 1 | 723 | Planned | Planned interruption | Sub Upgrade
1502 |  | SKE1919 | TE202 CCT15 (DB J147 - Old TE2 CCT11 - Museum) |  | Arthur Street | 2025-03-16 07:00 | 45732.2917 | 2025-03-16 19:14 | 45732.8014 | 0.021637 | 2.9478e-05 | 1 | 734 | Planned | Planned interruption | Sub Upgrade
1503 |  | JDJ157 | CB W470 - ABS W337 |  | St Andrews | 2025-03-17 08:30 | 45733.3542 | 2025-03-17 08:33 | 45733.3562 | 0.0041563 | 0.0013854 | 47 | 141 | Planned | Planned interruption | OH Refurbishment
1504 |  | JDJ157 | ABS W337 |  | St Andrews | 2025-03-17 08:30 | 45733.3542 | 2025-03-17 16:42 | 45733.6958 | 1.9579 | 0.0039795 | 135 | 66420 | Planned | Planned interruption | OH Refurbishment
1505 |  | JDJ157 | Links L294 - CB W470 |  | St Andrews | 2025-03-17 08:40 | 45733.3611 | 2025-03-17 08:41 | 45733.3618 | 2.9478e-05 | 2.9478e-05 | 1 | 1 | Planned | Planned interruption | OH Refurbishment
1506 |  | JDJ157 | Links @ P#40903 - Links L294 |  | St Andrews | 2025-03-17 08:45 | 45733.3646 | 2025-03-17 16:23 | 45733.6826 | 0.10801 | 0.00023582 | 8 | 3664 | Planned | Planned interruption | OH Refurbishment
1507 |  | JDJ157 | Links @ P#40903 - Links L294 |  | St Andrews | 2025-03-17 08:45 | 45733.3646 | 2025-03-17 16:56 | 45733.7056 | 0.014474 | 2.9478e-05 | 1 | 491 | Planned | Planned interruption | OH Refurbishment
1508 |  | 5029 | Tx B1981 |  | Normanby | 2025-03-17 10:57 | 45733.4563 | 2025-03-17 10:59 | 45733.4576 | 5.8955e-05 | 2.9478e-05 | 1 | 2 | Planned | Planned interruption | Tap Change
1509 |  | 5032 | TE172 CCT18-LB S47-DB S48-DB S49-DB S50 |  | Hobbs Street | 2025-03-17 15:28 | 45733.6444 | 2025-03-18 14:53 | 45734.6201 | 0.16566 | 0.00011791 | 4 | 5620 | Unplanned | Defective equipment | DB S47 replacement due to fire
1510 |  | 5032 | LB S47 |  | Hobbs Street | 2025-03-17 15:28 | 45733.6444 | 2025-03-18 15:10 | 45734.6319 | 0.083834 | 5.8955e-05 | 2 | 2844 | Unplanned | Defective equipment | DB S47 replacement due to fire
1511 |  | 5032 | DB S48 |  | Hobbs Street | 2025-03-17 15:28 | 45733.6444 | 2025-03-18 15:25 | 45734.6424 | 0.084719 | 5.8955e-05 | 2 | 2874 | Unplanned | Defective equipment | DB S47 replacement due to fire
1512 |  | 5032 | DB S49 |  | Hobbs Street | 2025-03-17 15:28 | 45733.6444 | 2025-03-18 15:28 | 45734.6444 | 0.084896 | 5.8955e-05 | 2 | 2880 | Unplanned | Defective equipment | DB S47 replacement due to fire
1513 |  | 5032 | DB S50 |  | Hobbs Street | 2025-03-17 15:28 | 45733.6444 | 2025-03-18 15:41 | 45734.6535 | 0.47114 | 0.00032425 | 11 | 15983 | Unplanned | Defective equipment | DB S47 replacement due to fire
1514 |  | JDJ157 | Links L294 - CB W470 |  | St Andrews | 2025-03-17 16:34 | 45733.6903 | 2025-03-17 16:40 | 45733.6944 | 0.00017687 | 2.9478e-05 | 1 | 6 | Planned | Planned interruption | OH Refurbishment
1515 |  | JDJ157 | CB W470 - ABS W337 |  | St Andrews | 2025-03-17 16:35 | 45733.691 | 2025-03-17 16:42 | 45733.6958 | 0.0096981 | 0.0013854 | 47 | 329 | Planned | Planned interruption | OH Refurbishment
1516 |  | 5078 | PLPTCB2 to L234 |  | Sutherland | 2025-03-18 03:34 | 45734.1486 | 2025-03-18 04:17 | 45734.1785 | 0.0012675 | 2.9478e-05 | 1 | 43 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364
1517 |  | 5078 | From L234 |  | Sutherland | 2025-03-18 03:34 | 45734.1486 | 2025-03-18 04:42 | 45734.1958 | 0.19443 | 0.0028593 | 97 | 6596 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364
1518 |  | 5078 | From L1239 |  | Sutherland | 2025-03-18 03:34 | 45734.1486 | 2025-03-18 05:19 | 45734.2215 | 0.083569 | 0.0007959 | 27 | 2835 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364
1519 |  | 5078 | PLPTCB2 to L234 |  | Sutherland | 2025-03-18 04:39 | 45734.1937 | 2025-03-18 04:42 | 45734.1958 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Unplanned | Vegetation | Gum Tree Branch on Line at Pole #26364
1520 |  | SKE1929 | ABS L722 to end |  | Highfield | 2025-03-18 09:00 | 45734.375 | 2025-03-19 14:41 | 45735.6118 | 0.6825 | 0.00038321 | 13 | 23153 | Planned | Planned interruption | Replace ABS
1521 |  | SRT288 | Pole #29337 to end |  | Otaio | 2025-03-19 08:30 | 45735.3542 | 2025-03-19 08:36 | 45735.3583 | 0.00070746 | 0.00011791 | 4 | 24 | Planned | Planned interruption | Makikihi Line Maintenance
1522 |  | SRT288 | Pole #43015 - Pole #29337 - Fuses TOA84 |  | Otaio | 2025-03-19 08:30 | 45735.3542 | 2025-03-19 15:52 | 45735.6611 | 0.7166 | 0.0016213 | 55 | 24310 | Planned | Planned interruption | Makikihi Line Maintenance
1523 |  | SRT288 | Fuses TOA84 |  | Otaio | 2025-03-19 08:30 | 45735.3542 | 2025-03-19 16:08 | 45735.6722 | 0.013501 | 2.9478e-05 | 1 | 458 | Planned | Planned interruption | Makikihi Line Maintenance
1524 |  | HTR108/5031 | From G112 |  | Winchester | 2025-03-19 09:00 | 45735.375 | 2025-03-19 09:34 | 45735.3986 | 0.024054 | 0.00070746 | 24 | 816 | Unplanned | Human error | Switching error - Paperwork had been redated but faultman had incorrect dated switching.
1525 |  | SRT288 | Pole #29337 to end |  | Otaio | 2025-03-19 16:30 | 45735.6875 | 2025-03-19 16:32 | 45735.6889 | 0.00023582 | 0.00011791 | 4 | 8 | Planned | Planned interruption | Makikihi Line Maintenance
1526 |  | 5079 | Fuses TO D1043 |  | Waitohi | 2025-03-19 17:26 | 45735.7264 | 2025-03-19 21:19 | 45735.8882 | 0.013737 | 5.8955e-05 | 2 | 466 | Unplanned | Defective equipment | Faulty Transformer
1527 |  | ACD189 | ABS W324 - ABS W457 |  | St Andrews | 2025-03-21 09:00 | 45737.375 | 2025-03-21 11:27 | 45737.4771 | 0.064998 | 0.00044216 | 15 | 2205 | Planned | Planned interruption | Replace Pole
1528 |  | ACD188 | CB W664 - ABS W263 - ABS W577 + Tx A191 |  | Waihaorunga | 2025-03-21 09:01 | 45737.3757 | 2025-03-21 13:49 | 45737.5757 | 0.38203 | 0.0013265 | 45 | 12960 | Planned | Planned interruption | New Line to Tx A1631
1529 |  | ACD188 | TO A192 |  | Waihaorunga | 2025-03-21 09:01 | 45737.3757 | 2025-03-21 13:59 | 45737.5826 | 0.043922 | 0.00014739 | 5 | 1490 | Planned | Planned interruption | New Line to Tx A1631
1530 |  | 5080 | G251 - G204 |  | Speechley | 2025-03-23 00:23 | 45739.016 | 2025-03-23 02:37 | 45739.109 | 0.21725 | 0.0016213 | 55 | 7370 | Unplanned | Third party interference | Car v Pole #09898
1531 |  | 5080 | G204 |  | Speechley | 2025-03-23 00:23 | 45739.016 | 2025-03-23 07:11 | 45739.2993 | 1.0463 | 0.0025646 | 87 | 35496 | Unplanned | Third party interference | Car v Pole #09898
1532 |  | SRS059 | From TO D1404 - LG006 - D1404-04 |  | Geraldine Township | 2025-03-25 08:30 | 45741.3542 | 2025-03-25 17:18 | 45741.7208 | 0.077821 | 0.00014739 | 5 | 2640 | Planned | Planned interruption | Install new RMU G362 G363 G364 & TX D2148
1533 |  | GWM1267 | From TO D1260 |  | Milford | 2025-03-26 09:00 | 45742.375 | 2025-03-26 09:51 | 45742.4104 | 0.0030067 | 5.8955e-05 | 2 | 102 | Planned | Planned interruption | Tree Trimming
1534 |  | SRT301 | From Temp Links @ Pole #35566 |  | Waipopo | 2025-03-26 09:01 | 45742.3757 | 2025-03-26 15:59 | 45742.666 | 0.036965 | 8.8433e-05 | 3 | 1254 | Planned | Planned interruption | Install new LBS
1535 |  | SRT299 | Tx B2296 CCT 03 - Highlighted ICPs |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:30 | 45743.7292 | 0.38645 | 0.00067799 | 23 | 13110 | Planned | Planned interruption | Line Maintenance
1536 |  | SRT299 | Tx B2296 CCT 02 - Highlighted ICPs |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:36 | 45743.7333 | 0.35656 | 0.00061903 | 21 | 12096 | Planned | Planned interruption | Line Maintenance
1537 |  | SRT299 | 6 Andrew St |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:53 | 45743.7451 | 0.01748 | 2.9478e-05 | 1 | 593 | Planned | Planned interruption | Line Maintenance
1538 |  | SRT299 | 21 Bouverie St |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:44 | 45743.7389 | 0.017215 | 2.9478e-05 | 1 | 584 | Planned | Planned interruption | Line Maintenance
1539 |  | SRT299 | 31 Bouverie St |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:46 | 45743.7403 | 0.017274 | 2.9478e-05 | 1 | 586 | Planned | Planned interruption | Line Maintenance
1540 |  | SRT299 | 20 & 22 Bouverie St |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:45 | 45743.7396 | 0.034489 | 5.8955e-05 | 2 | 1170 | Planned | Planned interruption | Line Maintenance
1541 |  | SRT299 | 3 Andrew St + 23, 24 & 33 Bouverie St |  | Grants Road | 2025-03-27 08:00 | 45743.3333 | 2025-03-27 17:48 | 45743.7417 | 0.069331 | 0.00011791 | 4 | 2352 | Planned | Planned interruption | Line Maintenance
1542 |  | SRS042 | TO A841 - DB3255 ICP1 - DB3255 ICP2 |  | Waihaorunga | 2025-03-27 09:00 | 45743.375 | 2025-03-27 13:44 | 45743.5722 | 0.42695 | 0.0015034 | 51 | 14484 | Planned | Planned interruption | Replace DB3255 & maintain DB3256, DB3257 & DB3254
1543 |  | SRS042 | DB3255 ICP1 + DB3255 ICP2 |  | Waihaorunga | 2025-03-27 09:00 | 45743.375 | 2025-03-27 14:05 | 45743.5868 | 0.017981 | 5.8955e-05 | 2 | 610 | Planned | Planned interruption | Replace DB3255 & maintain DB3256, DB3257 & DB3254
1544 |  | 5033 | TX A86 |  | Otaio | 2025-03-28 13:15 | 45744.5521 | 2025-03-28 13:18 | 45744.5542 | 8.8433e-05 | 2.9478e-05 | 1 | 3 | Unplanned | Defective equipment | TX Tap change for voltage
1545 |  | 3799 | T626 - T775(T490) |  | Rolleston Road | 2025-03-29 20:47 | 45745.866 | 2025-03-29 20:55 | 45745.8715 | 0.009197 | 0.0011496 | 39 | 312 | Unplanned | Unknown | Possible line clash past ABS T675
1546 |  | 3799 | T775(T490) |  | Rolleston Road | 2025-03-29 20:47 | 45745.866 | 2025-03-29 22:01 | 45745.9174 | 0.32284 | 0.0043627 | 148 | 10952 | Unplanned | Unknown | Possible line clash past ABS T675
1547 |  | 3800 | T675 |  | Rolleston Road | 2025-03-30 10:47 | 45746.4493 | 2025-03-30 12:20 | 45746.5139 | 0.013707 | 0.00014739 | 5 | 465 | Unplanned | Defective equipment | Conductor repair @ P#488723
1548 |  | JJV153 | E148-03 (Motor Camp) |  | Lakeside Drive | 2025-03-31 07:26 | 45747.3097 | 2025-03-31 07:45 | 45747.3229 | 0.00056008 | 2.9478e-05 | 1 | 19 | Planned | Planned interruption | Replace RMU (M146, M147)
1549 |  | JJV153 | E148-04 (Caravan Points) |  | Lakeside Drive | 2025-03-31 07:26 | 45747.3097 | 2025-03-31 07:45 | 45747.3229 | 0.00056008 | 2.9478e-05 | 1 | 19 | Planned | Planned interruption | Replace RMU (M146, M147)
1550 |  | JJV153 | E148-02 (Boat Club) |  | Lakeside Drive | 2025-03-31 07:58 | 45747.3319 | 2025-03-31 16:16 | 45747.6778 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Replace RMU (M146, M147)
1551 |  | JJV153 | E148-05 (Toilets) |  | Lakeside Drive | 2025-03-31 07:58 | 45747.3319 | 2025-03-31 16:16 | 45747.6778 | 0.01468 | 2.9478e-05 | 1 | 498 | Planned | Planned interruption | Replace RMU (M146, M147)
1552 |  | JJV153 | E262 '01' (Ice Rink) |  | Lakeside Drive | 2025-03-31 07:58 | 45747.3319 | 2025-03-31 16:15 | 45747.6771 | 0.01465 | 2.9478e-05 | 1 | 497 | Planned | Planned interruption | Replace RMU (M146, M147)
1553 |  | HTR104 | ABS L803 - ABS L806 |  | Hadlow | 2025-03-31 08:56 | 45747.3722 | 2025-03-31 13:40 | 45747.5694 | 1.2725 | 0.0044806 | 152 | 43168 | Planned | Planned interruption | Tree Cutting
1554 |  | HTR105 | ABS L175 |  | Normanby | 2025-03-31 13:00 | 45747.5417 | 2025-03-31 15:29 | 45747.6451 | 0.043922 | 0.00029478 | 10 | 1490 | Planned | Planned interruption | Tree Cutting
1555 |  | JJV153 | E148-03 (Motor Camp) |  | Lakeside Drive | 2025-03-31 16:18 | 45747.6792 | 2025-03-31 16:38 | 45747.6931 | 0.00058955 | 2.9478e-05 | 1 | 20 | Planned | Planned interruption | Replace RMU (M146, M147)
1556 |  | JJV153 | E148-04 (Caravan Points) |  | Lakeside Drive | 2025-03-31 16:18 | 45747.6792 | 2025-03-31 16:38 | 45747.6931 | 0.00058955 | 2.9478e-05 | 1 | 20 | Planned | Planned interruption | Replace RMU (M146, M147)
1557 |  | 5129 | CB W196 to W171 |  | Morven | 2024-10-09 16:32 | 45574.6889 | 2024-10-09 17:38 | 45574.7347 | 0.07393 | 0.0011202 | 38 | 2508 | Unplanned | Vegetation | Trees on line past W171
1558 |  | 5129 | W171 to end |  | Morven | 2024-10-09 16:32 | 45574.6889 | 2024-10-09 20:24 | 45574.85 | 0.054711 | 0.00023582 | 8 | 1856 | Unplanned | Vegetation | Trees on line past W171
1559 |  | 3827 | G297 to end |  | Winchester | 2024-12-09 05:02 | 45635.2097 | 2024-12-09 05:56 | 45635.2472 | 0.54439 | 0.010081 | 342 | 18468 | Unplanned | Vegetation | Branch on line
1560 |  | 4401 | M272 closed |  | M159 | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:06 | 45397.9208 | 0.42917 | 0.002034 | 69 | 14559 | Unplanned | Unknown | Unknown - possible bird strike
1561 |  | 4401 | M272 closed |  | M158 | 2024-04-15 18:35 | 45397.7743 | 2024-04-15 22:06 | 45397.9208 | 0.10574 | 0.00050112 | 17 | 3587 | Unplanned | Unknown | Unknown - possible bird strike
1562 |  | 5040 | M272 + M158 + M159 |  | M159 | 2024-05-09 11:08 | 45421.4639 | 2024-05-09 12:00 | 45421.5 | 0.10577 | 0.002034 | 69 | 3588 | Unplanned | Defective equipment | Repair conductor @ P#21659
1563 |  | 5040 | M272 + M158 + M159 |  | M158 | 2024-05-09 11:08 | 45421.4639 | 2024-05-09 12:00 | 45421.5 | 0.026058 | 0.00050112 | 17 | 884 | Unplanned | Defective equipment | Repair conductor @ P#21659
1564 |  | ACD153 | RMU M364 MS |  | M158 | 2024-06-26 09:07 | 45469.3799 | 2024-06-26 16:11 | 45469.6743 | 0.19998 | 0.00047164 | 16 | 6784 | Planned | Planned interruption | Red Tag Pole replacements
1565 |  | ACD153 | RMU M363 MS |  | M159 | 2024-06-26 09:07 | 45469.3799 | 2024-06-26 16:11 | 45469.6743 | 0.8749 | 0.0020634 | 70 | 29680 | Planned | Planned interruption | Red Tag Pole replacements
1566 |  | ¹ Extend table as necessary to disclose information for all individual interruptions