## CoverSheet
EDB Information Disclosure Requirements
Information Templates
Schedule 10a
| Company Name | Alpine Energy Limited
| Disclosure Date | 2026-08-31
| Disclosure Year (year ended) | 2026-03-31
Template for Schedule 10a
Prepared 2 June 2026.

## TOC
Table of Contents
Schedule | Schedule name
10a | REPORT ON INTERRUPTIONS

## Instructions
Disclosure Template Instructions
This document forms Schedule 10a to the Electricity Distribution Information Disclosure (Non-material) Amendment Determination 2026 [2026] NZCC 21.
The Schedules take the form of templates for use by EDBs when making disclosures under subclause 2.5.1 of the Electricity Distribution Information Disclosure Determination 2012, as amended.
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the last day of the current (disclosure) year should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (current year) is used to calculate disclosure years in the column headings that show above some of the tables and in labels adjacent to some entry cells. It is also used to calculate the ‘For year ended’ date in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2023").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to help guard against errors in data entry, some data entry cells test keyboard entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names, to values between 0% and 100%, or either a numeric entry or the text entry “N/A”. Where this occurs, a validation message will appear when data is being entered. These checks are applied to keyboard entries only and not, for example, to entries made using Excel’s copy and paste facility.
Inserting Additional Rows and Columns
The schedule 10a template may require additional rows to be inserted in tables marked 'include additional rows if needed' or similar. Column A schedule references should not be entered in additional rows, and should be deleted from additional rows that are created by copying and pasting rows that have schedule references.
Additional rows in the schedule 10a template must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S10a.Interruptions
[15 empty] | Company Name | Alpine Energy Limited
[15 empty] | For Year Ended | 2026-03-31
SCHEDULE 10a: REPORT ON INTERRUPTIONS
This schedule requires raw interruption data for the disclosure year. SAIDI and SAIFI is to be recorded using the multi-count approach.Where multiple feeders are affected, the interruption record is to be split into multiple interruptions, ie, one interruption record per feeder. This information is part of audited disclosure information (as defined in section 1.4 of this ID determination), and so is subject to the assurance report required by section 2.8.
sch ref
7 | 10a(i): Raw interruption data
8 |  | Interruption identifier | Circuit location | Sub-network (where applicable) | Feeder(s) affected by interruption | Start date (dd/mm/yyyy) | Start time (hh:mm:ss) | End date (dd/mm/yyyy) | End time (hh:mm:ss) | SAIDI value | SAIFI value | Number of ICPs interrupted | ICP interruption minutes | Planned or unplanned interruption (Class B or C) | Cause | Any explanation to help clarify the context of the interruption, including what the cause is if recorded as 'Other cause'
9 |  | 260325IM1Z5CDD | FUSES L830 |  | Timaru 2852 - Hadlow | 2025-04-01 08:30 | 45748.3542 | 2025-04-01 12:25 | 45748.5174 | 0.16861 | 0.0007175 | 25 | 5875 | B | Planned interruption | TREE CUTTING P#35319 - 35324
10 |  | 250402ABESXVRA | Transformer - B820 |  | Pareora CB7 - Holmestation | 2025-04-01 12:26 | 45748.5181 | 2025-04-01 14:35 | 45748.6076 | 0.0074046 | 5.74e-05 | 2 | 258 | C | DefectiveEquipment | Broken conductor at TX B820
11 |  | 260325ZZVBMOPN | ABS G310 |  | Geraldine G191 - Geraldine Township | 2025-04-01 13:00 | 45748.5417 | 2025-04-01 16:58 | 45748.7069 | 0.2459 | 0.0010332 | 36 | 8568 | B | Planned interruption | TREE TRIMMING BENNET RD
12 |  | 260325LKPUC545 | FUSES G112 |  | Temuka 03 - Winchester | 2025-04-02 09:00 | 45749.375 | 2025-04-02 15:08 | 45749.6306 | 0.25348 | 0.0006888 | 24 | 8832 | B | Planned interruption | Tree cutting p#03167-p#870517
13 |  | 250416GIK7K3CP | LVFeeder - D1247-01 |  | Rangitata 02 - Arundel | 2025-04-04 16:31 | 45751.6882 | 2025-04-04 19:44 | 45751.8222 | 0.083288 | 0.0015211 | 95 | 2944 | C | VegetationInZone | Hedge in lines
14 |  | 2508127RGKPAWR | Temuka |  | Rangitata 02 - Arundel | 2025-04-07 09:00 | 45754.375 | 2025-04-07 12:39 | 45754.5271 | 0.28913 | 0.0013202 | 46 | 10074 | B | Planned interruption | Planned Interruption Vegetation
15 |  | 260325RJZLGNMT | Fuses F815 |  | Timaru 2852 - Hadlow | 2025-04-07 10:00 | 45754.4167 | 2025-04-07 16:44 | 45754.6972 | 0.16233 | 0.0004018 | 14 | 5656 | B | Planned interruption | Replace pole #22801 & p#23498
16 |  | 250416ICYRDFLO | Fuses M355 |  | Tekapo M346 - Unwin Hut 33kV | 2025-04-08 08:10 | 45755.3403 | 2025-04-08 10:25 | 45755.434 | 0.023247 | 0.0001722 | 6 | 810 | C | CauseUnknown | Unknown Fault
17 |  | 250812IOHHIZ8O | Timaru |  | Timaru 2852 - Hadlow | 2025-04-09 08:30 | 45756.3542 | 2025-04-09 14:48 | 45756.6167 | 0.15188 | 0.0004018 | 14 | 5292 | B | Planned interruption | Planned Interruption Equipment
18 |  | 250812GIAAPZMI | Timaru |  | Pleasant Point CB4 - Totara Valley | 2025-04-09 09:00 | 45756.375 | 2025-04-09 16:08 | 45756.6722 | 0.049135 | 0.0001148 | 4 | 1712 | B | Planned interruption | Planned Interruption Vegetation
19 |  | 250812MR3AHYNN | Studholme |  | Studholme 09 - Morven | 2025-04-09 08:30 | 45756.3542 | 2025-04-09 16:37 | 45756.6924 | 0.17694 | 0.0003731 | 13 | 6165 | B | Planned interruption | Notified Interruption Equipment
20 |  | 250416JPI0V7PJ | Transformer - D109 |  | Temuka 09 - Waitohi | 2025-04-10 06:05 | 45757.2535 | 2025-04-10 06:54 | 45757.2875 | 0.01105 | 0.0002583 | 9 | 385 | C | CauseUnknown | Unknown
21 |  | 2505142NNWZT3P | LVFeeder - A10-01 |  | Pareora CB4 - St Andrews | 2025-04-10 14:51 | 45757.6188 | 2025-04-10 19:23 | 45757.8076 | 0.30256 | 0.0050225 | 175 | 10542 | C | ThirdPartyInterference | Harvester V Lines
22 |  | 250812ET3QUM6N | Studholme |  | Studholme 09 - Morven | 2025-04-10 08:30 | 45757.3542 | 2025-04-10 17:50 | 45757.7431 | 0.20466 | 0.0003731 | 13 | 7131 | B | Planned interruption | Notified Interruption Equipment
23 |  | 250812DYPSQJ1W | Albury |  | Albury ABY2732 - Raincliff | 2025-04-14 09:00 | 45761.375 | 2025-04-14 11:07 | 45761.4632 | 0.032804 | 0.0002583 | 9 | 1143 | B | Planned interruption | Planned Interruption Equipment
24 |  | 250515P56CNNLU | LVFeeder - D1034-01 |  | Clandeboye No 1 T613 - Rolleston Road | 2025-04-15 09:46 | 45762.4069 | 2025-04-15 10:50 | 45762.4514 | 0.27417 | 0.0052808 | 184 | 9553 | C | CauseUnknown | Unknown
25 |  | 250515HLX4HDKY | Transformer - B100 |  | Pareora CB7 - Holmestation | 2025-04-15 07:13 | 45762.3007 | 2025-04-15 10:30 | 45762.4375 | 0.02827 | 0.0001435 | 5 | 985 | C | CauseUnknown | Unknown
26 |  | 250812PCLBOQZV | Bells Pond |  | Bells Pond CB13 - Waikakahi | 2025-04-15 09:07 | 45762.3799 | 2025-04-15 11:55 | 45762.4965 | 0.067503 | 0.0004018 | 14 | 2352 | B | Planned interruption | Planned Interruption Vegetation
27 |  | 250812C8XWP0EL | Timaru |  | Timaru 2852 - Hadlow | 2025-04-16 09:01 | 45763.3757 | 2025-04-16 15:06 | 45763.6292 | 0.12571 | 0.0003444 | 12 | 4380 | B | Planned interruption | Planned Interruption Vegetation
28 |  | 2505159VGFQT77 | ABS G177 to Fuses G159 |  | Geraldine G156 - Woodbury | 2025-04-17 06:06 | 45764.2542 | 2025-04-17 12:07 | 45764.5049 | 0.15257 | 0.0019803 | 69 | 5316 | C | ThirdPartyInterference | Car V Pole
29 |  | 250407Q2CW5LI3 | B197 |  | Timaru 2832 - Grants Road | 2025-04-17 09:00 | 45764.375 | 2025-04-17 13:22 | 45764.5569 | 0.12031 | 0.0004592 | 16 | 4192 | B | Planned interruption | Planned Interruption Equipment
30 |  | 250417AGO8RPEP | Studholme |  | Pareora CB4 - St Andrews | 2025-04-17 12:40 | 45764.5278 | 2025-04-17 15:35 | 45764.6493 | 0.070315 | 0.0004018 | 14 | 2450 | B | Planned interruption | Planned Interruption Equipment
31 |  | 250515HYJYOVTP | ICP's fed from pole #40993 |  | Pareora CB4 - St Andrews | 2025-04-19 15:43 | 45766.6549 | 2025-04-19 18:10 | 45766.7569 | 0.041242 | 0.0003157 | 11 | 1437 | C | DefectiveEquipment | Pole fire at service fuses
32 |  | 250812ZJLES8YP | ABS L340 to links L376 |  | WSS CB11 Waipopo | 2025-04-21 23:09 | 45768.9646 | 2025-04-22 05:34 | 45769.2319 | 1.2771 | 0.015498 | 540 | 44499 | C | DefectiveEquipment | Broken Pin insulator
33 |  | 2504142QW2XQDS | Links L138 |  | WSS CB7 Arowhenua and LS1 | 2025-04-23 01:29 | 45770.0618 | 2025-04-23 01:58 | 45770.0819 | 0.092386 | 0.0031857 | 111 | 3219 | B | Planned interruption | Planned Interruption Equipment
34 |  | 250411PFFVSXM1 | D1415 |  | Temuka 03 - Winchester | 2025-04-23 03:05 | 45770.1285 | 2025-04-23 03:16 | 45770.1361 | 0.0006314 | 5.74e-05 | 2 | 22 | B | Planned interruption | Planned Interruption Equipment
35 |  | 250825NGGANY0Z | CB L1159 |  | Pleasant Point CB5 - Pleasant Point Township | 2025-04-23 08:15 | 45770.3438 | 2025-04-23 19:19 | 45770.8049 | 0.023305 | 0.0033292 | 116 | 812 | C | HumanError | Replace 500KVA
36 |  | 250812BBQXSIE9 | Timaru |  | Pleasant Point CB5 - Pleasant Point Township | 2025-04-23 08:30 | 45770.3542 | 2025-04-23 18:00 | 45770.75 | 0.80406 | 0.0014637 | 51 | 28016 | B | Planned interruption | Notified Interruption Equipment
37 |  | 250825QVYP55JD | B1349 |  | Timaru 2952 - Highfield | 2025-04-25 07:48 | 45772.325 | 2025-04-25 09:15 | 45772.3854 | 0.094079 | 0.0012628 | 44 | 3278 | C | DefectiveEquipment | Unknown
38 |  | 250409FM20BRAO | D1006 |  | Geraldine G194 - Speechley | 2025-04-26 10:15 | 45773.4271 | 2025-04-26 14:24 | 45773.6 | 0.0071463 | 2.87e-05 | 1 | 249 | B | Planned interruption | Notified Interruption Equipment
39 |  | 250812PWWM0MCW | TOB719 |  | Pareora CB6 - Normanby | 2025-04-28 18:41 | 45775.7785 | 2025-04-28 19:59 | 45775.8326 | 0.0067158 | 8.6101e-05 | 3 | 234 | C | DefectiveEquipment | Broken X-arm
40 |  | 250410ISSRT7CC | Temuka |  | Geraldine G194 - Speechley | 2025-04-29 08:00 | 45776.3333 | 2025-04-29 08:28 | 45776.3528 | 0.021697 | 0.0007749 | 27 | 756 | B | Planned interruption | Planned Interruption Equipment
41 |  | 250410BFYOIS8S | Temuka |  | Geraldine G194 - Speechley | 2025-04-29 08:00 | 45776.3333 | 2025-04-29 08:50 | 45776.3681 | 0.097753 | 0.002296 | 80 | 3406 | B | Planned interruption | Planned Interruption Equipment
42 |  | 250812XE6WYDGL | ABS G119-Fuses G134-Links G138 |  | Geraldine G194 - Speechley | 2025-04-29 14:39 | 45776.6104 | 2025-04-29 15:06 | 45776.6292 | 0.061992 | 0.002296 | 80 | 2160 | C | DefectiveEquipment | Unknown
43 |  | 250409BWOC6SSO | Temuka |  | Geraldine G194 - Speechley | 2025-04-29 08:02 | 45776.3347 | 2025-04-29 16:51 | 45776.7021 | 0.46371 | 0.00094711 | 33 | 16157 | B | Planned interruption | Notified Interruption Equipment
44 |  | 250818KNPDAXI7 | Temuka |  | Geraldine G194 - Speechley | 2025-04-29 15:50 | 45776.6597 | 2025-04-29 16:13 | 45776.6757 | 0.039549 | 0.002296 | 80 | 1378 | B | Planned interruption | Planned Interruption Equipment
45 |  | 250812YGXHOCW9 | Fuses T122 |  | Temuka 02 - Milford | 2025-04-30 07:54 | 45777.3292 | 2025-04-30 08:43 | 45777.3632 | 0.021095 | 0.0004305 | 15 | 735 | C | DefectiveEquipment | Unknown
46 |  | 250812JFOAFGER | RMU L1321 |  | Wss Cb8 Woolworks Boiler | 2025-04-30 10:25 | 45777.434 | 2025-04-30 10:50 | 45777.4514 | 0.0007175 | 2.87e-05 | 1 | 25 | C | DefectiveEquipment | Unknown
47 |  | 250812XS3J1TSH | TO B1503 |  | Pleasant Point CB5 - Pleasant Point Township | 2025-05-01 12:58 | 45778.5403 | 2025-05-01 13:18 | 45778.5542 | 0.001148 | 5.74e-05 | 2 | 40 | C | DefectiveEquipment | Tap TX down due to high voltgaes
48 |  | 250812PDZMEPSY | G124-G327 |  | Geraldine G191 - Geraldine Township | 2025-05-01 16:40 | 45778.6944 | 2025-05-01 20:56 | 45778.8722 | 8.0298 | 0.066039 | 2301 | 279782 | C | DefectiveEquipment | Broken jumper at ABS G167
49 |  | 250825SMNBSC73 | F220 |  | Fairlie F380 - Fairlie Rural | 2025-05-02 10:00 | 45779.4167 | 2025-05-02 12:31 | 45779.5215 | 0.095342 | 0.0006314 | 22 | 3322 | C | DefectiveEquipment | Replaced damaged concrete pole
50 |  | 250416RX3CAS7W | Timaru |  | Timaru 2852 - Hadlow | 2025-05-05 09:00 | 45782.375 | 2025-05-05 14:44 | 45782.6139 | 0.3653 | 0.0010619 | 37 | 12728 | B | Planned interruption | Planned Interruption Equipment
51 |  | 250411J94JD5ME | D1006 |  | Geraldine G194 - Speechley | 2025-05-06 08:09 | 45783.3396 | 2025-05-06 16:08 | 45783.6722 | 0.23893 | 0.0005453 | 19 | 8325 | B | Planned interruption | Notified Interruption Equipment
52 |  | 2504160P3M1KKB | D879 |  | Temuka 08 - Temuka East | 2025-05-06 10:26 | 45783.4347 | 2025-05-06 16:37 | 45783.6924 | 0.10995 | 0.0003157 | 11 | 3831 | B | Planned interruption | Planned Interruption Equipment
53 |  | 250812FMIO6L7L | F422 -TX C414 |  | Fairlie F380 - Fairlie Rural | 2025-05-06 19:09 | 45783.7979 | 2025-05-07 16:50 | 45784.7014 | 0.048245 | 0.0001435 | 5 | 1681 | C | DefectiveEquipment | Fire at Pole 10877
54 |  | 250411UXFEG7IZ | Temuka |  | Geraldine G194 - Speechley | 2025-05-07 08:00 | 45784.3333 | 2025-05-07 08:06 | 45784.3375 | 0.011021 | 0.0018368 | 64 | 384 | B | Planned interruption | Notified Interruption Equipment
55 |  | 250812WSBSKS1V | Fuses W312 |  | Studholme 08 - Mount Studholme | 2025-05-07 09:26 | 45784.3931 | 2025-05-07 12:07 | 45784.5049 | 0.023104 | 0.0001435 | 5 | 805 | C | DefectiveEquipment | N/A
56 |  | 250411VX7WINRL | Temuka |  | Geraldine G194 - Speechley | 2025-05-07 08:00 | 45784.3333 | 2025-05-07 18:12 | 45784.7583 | 0.78001 | 0.0014063 | 49 | 27178 | B | Planned interruption | Notified Interruption Equipment
57 |  | 251119FPUGVQ91 | Temuka |  | Geraldine G194 - Speechley | 2025-05-07 17:33 | 45784.7312 | 2025-05-07 17:50 | 45784.7431 | 0.031226 | 0.0018368 | 64 | 1088 | B | Planned interruption | Notified Interruption Equipment
58 |  | 250411SVM6LILS | Temuka |  | Geraldine G194 - Speechley | 2025-05-08 08:00 | 45785.3333 | 2025-05-08 08:17 | 45785.3451 | 0.031226 | 0.0018368 | 64 | 1088 | B | Planned interruption | Notified Interruption Equipment
59 |  | 2504110B6CPXLE | Temuka |  | Geraldine G194 - Speechley | 2025-05-08 08:09 | 45785.3396 | 2025-05-08 16:08 | 45785.6722 | 0.64828 | 0.0014063 | 49 | 22588 | B | Planned interruption | Notified Interruption Equipment
60 |  | 251114NSWSNKZF | Temuka |  | Geraldine G194 - Speechley | 2025-05-08 15:56 | 45785.6639 | 2025-05-08 16:17 | 45785.6785 | 0.038573 | 0.0018368 | 64 | 1344 | B | Planned interruption | Notified Interruption Equipment
61 |  | 250812EDXYQYKO | ABS L243 to end |  | Pleasant Point CB1 - Waitawa | 2025-05-09 06:28 | 45786.2694 | 2025-05-09 13:58 | 45786.5819 | 2.0443 | 0.016244 | 566 | 71230 | C | DefectiveEquipment | Broken Pin insulator
62 |  | 250812EKQSEPQG | D1556 |  | Temuka 02 - Milford | 2025-05-10 07:38 | 45787.3181 | 2025-05-10 09:10 | 45787.3819 | 0.0026404 | 2.87e-05 | 1 | 92 | C | Wildlife | Goose vs Lines
63 |  | 2504097MDLZQ58 | D1006 |  | Geraldine G194 - Speechley | 2025-05-10 09:43 | 45787.4049 | 2025-05-10 12:32 | 45787.5222 | 0.0048503 | 2.87e-05 | 1 | 169 | B | Planned interruption | Notified Interruption Equipment
64 |  | 250422OEJJ5SKJ | Timaru |  | Timaru 2852 - Hadlow | 2025-05-12 09:01 | 45789.3757 | 2025-05-12 15:22 | 45789.6403 | 0.032804 | 8.6101e-05 | 3 | 1143 | B | Planned interruption | Planned Interruption Vegetation
65 |  | 2505065VCGS3OM | Timaru |  | Wss Cb11 Waipopo | 2025-05-12 09:03 | 45789.3771 | 2025-05-12 15:55 | 45789.6632 | 0.011824 | 2.87e-05 | 1 | 412 | B | Planned interruption | Planned Interruption Equipment
66 |  | 250812C9O7GBT8 | ABS T675 to end |  | Clandeboye No 1 T613 - Rolleston Road | 2025-05-12 22:02 | 45789.9181 | 2025-05-13 01:40 | 45790.0694 | 0.25735 | 0.0053382 | 186 | 8967 | C | Wildlife | Bird strike at pole conductors broke towards pole
67 |  | 2504223JXZPAHD | Studholme |  | Pareora CB4 - St Andrews | 2025-05-13 08:30 | 45790.3542 | 2025-05-13 08:43 | 45790.3632 | 0.020894 | 0.0016072 | 56 | 728 | B | Planned interruption | Notified Interruption Equipment
68 |  | 2504229Q5UWIUU | Studholme |  | Pareora CB4 - St Andrews | 2025-05-13 08:30 | 45790.3542 | 2025-05-13 16:20 | 45790.6806 | 1.6658 | 0.0036449 | 127 | 58043 | B | Planned interruption | Notified Interruption Equipment
69 |  | 250422R4WEXAZ8 | Studholme |  | Pareora CB4 - St Andrews | 2025-05-13 16:00 | 45790.6667 | 2025-05-13 16:04 | 45790.6694 | 0.0064288 | 0.0016072 | 56 | 224 | B | Planned interruption | Notified Interruption Equipment
70 |  | 250812W9IQKJDZ | ABS L167 to end |  | Pareora CB6 - Normanby | 2025-05-14 10:00 | 45791.4167 | 2025-05-14 11:02 | 45791.4597 | 0.028471 | 0.0004592 | 16 | 992 | C | DefectiveEquipment | Emergency outage for binder repairs
71 |  | 250502IRS28XCL | Temuka |  | Geraldine G194 - Speechley | 2025-05-15 08:00 | 45792.3333 | 2025-05-15 08:17 | 45792.3451 | 0.031226 | 0.0018368 | 64 | 1088 | B | Planned interruption | Notified Interruption Equipment
72 |  | 250812Y96VNCT3 | TOD1236 |  | Rangitata 03 - Mahan Road | 2025-05-15 10:35 | 45792.441 | 2025-05-15 10:54 | 45792.4542 | 0.0027265 | 0.0001435 | 5 | 95 | C | ThirdPartyInterference | emergency repair to LV consumer
73 |  | 250424CPD27SHH | Albury |  | Albury ABY2732 - Raincliff | 2025-05-15 10:00 | 45792.4167 | 2025-05-15 13:09 | 45792.5479 | 0.041472 | 0.0002583 | 9 | 1445 | B | Planned interruption | Planned Interruption Equipment
74 |  | 250502TLM1KKJA | Temuka |  | Geraldine G194 - Speechley | 2025-05-15 08:13 | 45792.3424 | 2025-05-15 16:08 | 45792.6722 | 0.63264 | 0.0014063 | 49 | 22043 | B | Planned interruption | Notified Interruption Equipment
75 |  | 250502WIY8GTEG | Temuka |  | Geraldine G194 - Speechley | 2025-05-15 15:56 | 45792.6639 | 2025-05-15 16:17 | 45792.6785 | 0.038573 | 0.0018368 | 64 | 1344 | B | Planned interruption | Notified Interruption Equipment
76 |  | 250428YPYSPCQT | Timaru |  | Timaru 2952 - Highfield | 2025-05-15 08:00 | 45792.3333 | 2025-05-15 17:38 | 45792.7347 | 1.9107 | 0.0036449 | 127 | 66576 | B | Planned interruption | Notified Interruption Equipment
77 |  | 250812577A97OI | ABS W461 to end |  | Studholme 09 - Morven | 2025-05-15 22:44 | 45792.9472 | 2025-05-16 14:50 | 45793.6181 | 0.66728 | 0.010189 | 355 | 23250 | C | Wildlife | Bird vs Line
78 |  | 250812JJ3L1TYU | TO A1126 |  | Studholme 01 - Otaio | 2025-05-16 08:00 | 45793.3333 | 2025-05-16 09:51 | 45793.4104 | 0.0031857 | 2.87e-05 | 1 | 111 | C | Wildlife | Bird Strike
79 |  | 250812SEECCWTZ | Fuses W266 to end |  | Studholme 09 - Morven | 2025-05-17 08:05 | 45794.3368 | 2025-05-17 08:37 | 45794.359 | 0.0082656 | 0.0002583 | 9 | 288 | C | DefectiveEquipment | No power 2 blown fuse
80 |  | 250812UGOFPA1B | ABS W461 to end |  | Studholme 09 - Morven | 2025-05-17 23:12 | 45794.9667 | 2025-05-18 03:04 | 45795.1278 | 0.36036 | 0.010189 | 355 | 12556 | C | Wildlife | Bird vs Line
81 |  | 250812CKHLVKKJ | Temuka |  | Geraldine G194 - Speechley | 2025-05-19 12:00 | 45796.5 | 2025-05-19 13:31 | 45796.5632 | 0.028729 | 0.0003157 | 11 | 1001 | B | Planned interruption | Planned Interruption Vegetation
82 |  | 2505023BJFCOIX | Temuka |  | Geraldine G194 - Speechley | 2025-05-19 09:00 | 45796.375 | 2025-05-19 15:40 | 45796.6528 | 0.14924 | 0.0003731 | 13 | 5200 | B | Planned interruption | Planned Interruption-Vegetation
83 |  | 250508YVNCJZ9Q | Studholme |  | Studholme 09 - Morven | 2025-05-19 09:00 | 45796.375 | 2025-05-19 15:59 | 45796.666 | 0.13228 | 0.0003157 | 11 | 4609 | B | Planned interruption | Planned Interruption Equipment
84 |  | 250428CF7MXOWA | Temuka |  | Geraldine G194 - Speechley | 2025-05-20 08:30 | 45797.3542 | 2025-05-20 08:41 | 45797.3618 | 0.020205 | 0.0018368 | 64 | 704 | B | Planned interruption | Notified Interruption Equipment
85 |  | 2504284D2RZS2F | Temuka |  | Geraldine G194 - Speechley | 2025-05-20 08:30 | 45797.3542 | 2025-05-20 15:45 | 45797.6562 | 0.024969 | 5.74e-05 | 2 | 870 | B | Planned interruption | Notified Interruption Equipment
86 |  | 250428MWZEIMPQ | Temuka |  | Geraldine G194 - Speechley | 2025-05-20 15:34 | 45797.6486 | 2025-05-20 15:45 | 45797.6562 | 0.020205 | 0.0018368 | 64 | 704 | B | Planned interruption | Notified Interruption Equipment
87 |  | 250428ZXHA6YIX | Temuka |  | Geraldine G194 - Speechley | 2025-05-21 08:30 | 45798.3542 | 2025-05-21 08:40 | 45798.3611 | 0.012054 | 0.0012054 | 42 | 420 | B | Planned interruption | Notified Interruption Equipment
88 |  | 250428YB0DB9ZI | Albury |  | Fairlie F380 - Fairlie Rural | 2025-05-21 13:01 | 45798.5424 | 2025-05-21 13:46 | 45798.5736 | 0.063284 | 0.0014063 | 49 | 2205 | B | Planned interruption | Notified Interruption Equipment
89 |  | 250428HQ1PJUJO | Temuka |  | Geraldine G194 - Speechley | 2025-05-21 08:30 | 45798.3542 | 2025-05-21 16:30 | 45798.6875 | 0.27363 | 0.0006314 | 22 | 9534 | B | Planned interruption | Notified Interruption Equipment
90 |  | 250430EYJPV755 | Bell's Pond |  | Bells Pond CB11 - Waihao Downs | 2025-05-21 09:00 | 45798.375 | 2025-05-21 16:00 | 45798.6667 | 0.036162 | 8.6101e-05 | 3 | 1260 | B | Planned interruption | Planned Interruption Equipment
91 |  | 250428CTLI8LFW | Temuka |  | Geraldine G194 - Speechley | 2025-05-21 15:49 | 45798.659 | 2025-05-21 16:16 | 45798.6778 | 0.032546 | 0.0012054 | 42 | 1134 | B | Planned interruption | Notified Interruption Equipment
92 |  | 2508128Q2WWKFK | TX D1446 |  | Rangitata 04 - Main South Road | 2025-05-22 09:39 | 45799.4021 | 2025-05-22 10:32 | 45799.4389 | 0.0015211 | 2.87e-05 | 1 | 53 | C | Wildlife | Bird V lines
93 |  | 250819F6WMYWP8 | A1305 |  | Studholme 01 - Otaio | 2025-05-09 09:52 | 45786.4111 | 2025-05-22 12:50 | 45799.5347 | 0.54238 | 2.87e-05 | 1 | 18898 | B | Planned interruption | Planned Interruption Equipment
94 |  | 250428N6JO8LUQ | Studholme |  | Pareora CB6 - Normanby | 2025-05-22 09:00 | 45799.375 | 2025-05-22 13:43 | 45799.5715 | 0.23554 | 0.0008323 | 29 | 8207 | B | Planned interruption | Planned Interruption Equipment
95 |  | 2504303LTOCIWS | Bell's Pond |  | Bells Pond CB11 - Waihao Downs | 2025-05-22 09:00 | 45799.375 | 2025-05-22 14:46 | 45799.6153 | 0.029791 | 8.6101e-05 | 3 | 1038 | B | Planned interruption | Planned Interruption Equipment
96 |  | 250812XH5HW7MK | Fuses T420 to end |  | Geraldine G156 - Woodbury | 2025-05-24 14:18 | 45801.5958 | 2025-05-24 15:33 | 45801.6479 | 0.06027 | 0.0008036 | 28 | 2100 | C | CauseUnknown | Low voltage alarm
97 |  | 250505RSR69SNK | B2012 |  | Timaru 2762 - AEL Yard | 2025-05-24 08:28 | 45801.3528 | 2025-05-24 15:51 | 45801.6604 | 0.038143 | 8.6101e-05 | 3 | 1329 | B | Planned interruption | Planned Interruption Equipment
98 |  | 250505ND48COVW | Temuka |  | Geraldine G194 - Speechley | 2025-05-27 08:31 | 45804.3549 | 2025-05-27 08:49 | 45804.3674 | 0.020148 | 0.0011193 | 39 | 702 | B | Planned interruption | Notified Interruption Equipment
99 |  | 250505WM8VRPG4 | Temuka |  | Geraldine G194 - Speechley | 2025-05-27 08:31 | 45804.3549 | 2025-05-27 16:36 | 45804.6917 | 0.26387 | 0.0005453 | 19 | 9194 | B | Planned interruption | Notified Interruption Equipment
100 |  | 250812WZ4CXLWE | Fuses W183 |  | Bells Pond CB1 - Waihuna | 2025-05-27 16:37 | 45804.6924 | 2025-05-27 17:00 | 45804.7083 | 0.0026404 | 0.0001148 | 4 | 92 | C | Wildlife | Blown fuse
101 |  | 250505UPYOK1LF | Temuka |  | Geraldine G194 - Speechley | 2025-05-27 17:00 | 45804.7083 | 2025-05-27 17:07 | 45804.7132 | 0.0078351 | 0.0011193 | 39 | 273 | B | Planned interruption | Notified Interruption Equipment
102 |  | 250505BU67C6PQ | TE19 |  | Grasmere Street 15 - Park Lane | 2025-05-27 08:30 | 45804.3542 | 2025-05-27 18:36 | 45804.775 | 1.3466 | 0.002296 | 80 | 46920 | B | Planned interruption | Notified Interruption Equipment
103 |  | 250505EPOLVVVZ | Temuka |  | Geraldine G194 - Speechley | 2025-05-28 08:32 | 45805.3556 | 2025-05-28 15:46 | 45805.6569 | 0.19499 | 0.0004592 | 16 | 6794 | B | Planned interruption | Notified Interruption Equipment
104 |  | 250505IGZUQQDF | TE19 |  | Grasmere Street 15 - Park Lane | 2025-05-28 08:30 | 45805.3542 | 2025-05-28 17:15 | 45805.7188 | 0.95173 | 0.0018655 | 65 | 33161 | B | Planned interruption | Notified Interruption Equipment
105 |  | 250507WHEXMJOA | TE19 |  | Grasmere Street 15 - Park Lane | 2025-05-29 08:30 | 45806.3542 | 2025-05-29 11:50 | 45806.4931 | 0.0574 | 0.000287 | 10 | 2000 | B | Planned interruption | Notified Interruption Equipment
106 |  | 2505059WPOJB63 | Temuka |  | Geraldine G194 - Speechley | 2025-05-29 08:30 | 45806.3542 | 2025-05-29 13:30 | 45806.5625 | 0.13013 | 0.0004592 | 16 | 4534 | B | Planned interruption | Notified Interruption Equipment
107 |  | 250812RUNSME6N | ABS W675 to Fuses W319 |  | Studholme 01 - Otaio | 2025-05-30 07:56 | 45807.3306 | 2025-05-30 10:43 | 45807.4465 | 0.21344 | 0.0024395 | 85 | 7437 | C | DefectiveEquipment | Loose king bolt at pole
108 |  | 250516SRFWNP9W | Timaru |  | Pleasant Point CB2 - Sutherlands | 2025-05-30 09:35 | 45807.3993 | 2025-05-30 12:52 | 45807.5361 | 0.2205 | 0.0011193 | 39 | 7683 | B | Planned interruption | Planned Interruption Vegetation
109 |  | 250515UPLSK6IS | Temuka |  | Rangitata 12 - Orton | 2025-05-30 09:00 | 45807.375 | 2025-05-30 13:38 | 45807.5681 | 0.13564 | 0.0004879 | 17 | 4726 | B | Planned interruption | Planned Interruption Equipment
110 |  | 250825SVGBVZPS | F248 to end |  | Fairlie F380 - Fairlie Rural | 2025-05-30 16:14 | 45807.6764 | 2025-05-30 21:01 | 45807.8757 | 1.0587 | 0.0072037 | 251 | 36889 | C | DefectiveEquipment | 11kv Line on ground
111 |  | 250812WUOLONKB | ABS F277 |  | Fairlie F380 - Fairlie Rural | 2025-05-31 05:32 | 45808.2306 | 2025-05-31 12:31 | 45808.5215 | 0.5135 | 0.0024108 | 84 | 17892 | C | VegetationInZone | Wind Tree broke line
112 |  | 250812W5UGW8X1 | ABS L817 |  | Timaru 2852 - Hadlow | 2025-05-31 10:25 | 45808.434 | 2025-05-31 13:15 | 45808.5521 | 0.31886 | 0.0027265 | 95 | 11110 | C | DefectiveEquipment | Line down Binder failure
113 |  | 250505H04EVGMP | Temuka |  | Geraldine G194 - Speechley | 2025-06-03 08:33 | 45811.3562 | 2025-06-03 16:07 | 45811.6715 | 0.088913 | 0.0002009 | 7 | 3098 | B | Planned interruption | Notified Interruption Equipment
114 |  | 250507JAMQTMSW | B1153 |  | Timaru 2702 - Morgans Road | 2025-06-04 06:00 | 45812.25 | 2025-06-04 06:09 | 45812.2562 | 0.012657 | 0.0014063 | 49 | 441 | B | Planned interruption | Notified Interruption Equipment
115 |  | 250516EXPPNTVA | Temuka |  | Geraldine G194 - Speechley | 2025-06-04 08:30 | 45812.3542 | 2025-06-04 08:39 | 45812.3604 | 0.010074 | 0.0011193 | 39 | 351 | B | Planned interruption | Notified Interruption Equipment
116 |  | 250516YKG3OSBW | Temuka |  | Geraldine G194 - Speechley | 2025-06-04 08:30 | 45812.3542 | 2025-06-04 13:22 | 45812.5569 | 0.15449 | 0.0005453 | 19 | 5383 | B | Planned interruption | Notified Interruption Equipment
117 |  | 250520T3TTA7FS | A611 |  | Studholme 07 - Waihaorunga | 2025-06-04 09:00 | 45812.375 | 2025-06-04 13:58 | 45812.5819 | 0.076974 | 0.0002583 | 9 | 2682 | B | Planned interruption | Planned Interruption Equipment
118 |  | 250516F676XXT3 | Temuka |  | Geraldine G194 - Speechley | 2025-06-04 15:33 | 45812.6479 | 2025-06-04 15:37 | 45812.6507 | 0.0044772 | 0.0011193 | 39 | 156 | B | Planned interruption | Notified Interruption Equipment
119 |  | 250507LNPZABZJ | B688 |  | Timaru 2952 - Highfield | 2025-06-04 08:30 | 45812.3542 | 2025-06-04 18:54 | 45812.7875 | 1.0535 | 0.0017794 | 62 | 36707 | B | Planned interruption | Notified Interruption Equipment
120 |  | 250507K7P9ZNN6 | B1153 |  | Timaru 2702 - Morgans Road | 2025-06-04 19:18 | 45812.8042 | 2025-06-04 19:28 | 45812.8111 | 0.014034 | 0.0014063 | 49 | 489 | B | Planned interruption | Notified Interruption Equipment
121 |  | 2508122ZBWZYFK | ABS M385 to Fuses M20 |  | Haldon-Lilybank M86 - Haldon-Lilybank | 2025-06-05 01:33 | 45813.0646 | 2025-06-05 18:14 | 45813.7597 | 0.47743 | 0.0018368 | 64 | 16635 | C | DefectiveEquipment | Snow storm CB M82 Trip
122 |  | 250812CNWUYTBQ | Fuses D648 |  | Fairlie F380 - Fairlie Rural | 2025-06-04 20:54 | 45812.8708 | 2025-06-05 11:11 | 45813.466 | 0.15185 | 0.000287 | 10 | 5291 | C | Lightning | Lightening Blown Tx fuse
123 |  | 250812UWGPTTIH | M205 |  | Tekapo M205 - Godley | 2025-06-05 03:27 | 45813.1438 | 2025-06-05 12:52 | 45813.5361 | 0.82697 | 0.0021525 | 75 | 28814 | C | DefectiveEquipment | weather snow broken conductor
124 |  | 250512LSJ7ZGMY | Temuka |  | Geraldine G194 - Speechley | 2025-06-05 08:30 | 45813.3542 | 2025-06-05 12:48 | 45813.5333 | 0.021238 | 8.6101e-05 | 3 | 740 | B | Planned interruption | Notified Interruption Equipment
125 |  | 2505149T2IEKDH | D711 |  | Temuka 01 - Temuka West | 2025-06-06 09:25 | 45814.3924 | 2025-06-06 16:14 | 45814.6764 | 0.7043 | 0.001722 | 60 | 24540 | B | Planned interruption | Notified Interruption Equipment
126 |  | 250812YMJFDNPT | CB2832 minus L590 |  | Timaru 2832 - Grants Road | 2025-06-06 20:59 | 45814.8743 | 2025-06-07 02:25 | 45815.1007 | 13.813 | 0.042419 | 1478 | 481288 | C | DefectiveEquipment | Burnt jumper
127 |  | 250812SLONPHH2 | ABS F225 to end |  | Fairlie F380 - Fairlie Rural | 2025-06-07 02:51 | 45815.1188 | 2025-06-07 15:02 | 45815.6264 | 3.5397 | 0.0070889 | 247 | 123335 | C | DefectiveEquipment | Tripped on high current
128 |  | 250812DXKULDLS | CB F426 - Fuses F105 |  | Albury ABY2742 - Cave | 2025-06-07 01:18 | 45815.0542 | 2025-06-07 11:57 | 45815.4979 | 0.80897 | 0.0014063 | 49 | 28187 | C | AdverseWeather | Tx C135 on Fire
129 |  | 250812SRUV3HM5 | Fuses F252 to end |  | Fairlie F380 - Fairlie Rural | 2025-06-07 15:14 | 45815.6347 | 2025-06-07 15:34 | 45815.6486 | 0.00287 | 0.0001435 | 5 | 100 | C | VegetationInZone | Branches on ground
130 |  | 250812JW91CU7B | Fuses F108 to end |  | Albury ABY2742 - Cave | 2025-06-07 16:13 | 45815.6757 | 2025-06-07 16:57 | 45815.7063 | 0.0025256 | 5.74e-05 | 2 | 88 | C | VegetationOutZone | Tree branch online
131 |  | 250813PJMV9RQ7 | Fuses W527 to end |  | Bells Pond CB13 - Waikakahi | 2025-06-06 20:11 | 45814.841 | 2025-06-07 17:54 | 45815.7458 | 0.18698 | 0.0001435 | 5 | 6515 | C | DefectiveEquipment | Lines Down
132 |  | 250515ZXNJUBNS | Temuka |  | Geraldine G194 - Speechley | 2025-06-10 08:30 | 45818.3542 | 2025-06-10 14:27 | 45818.6021 | 0.089745 | 0.0002583 | 9 | 3127 | B | Planned interruption | Notified Interruption Equipment
133 |  | 250526ULO8MBCN | Temuka |  | Temuka 03 - Winchester | 2025-06-10 09:00 | 45818.375 | 2025-06-10 16:55 | 45818.7049 | 0.091869 | 0.0002009 | 7 | 3201 | B | Planned interruption | Planned Interruption Equipment
134 |  | 250527NDEFEEFT | Temuka |  | Temuka 02 - Milford | 2025-06-12 08:42 | 45820.3625 | 2025-06-12 14:10 | 45820.5903 | 0.30445 | 0.00097581 | 34 | 10608 | B | Planned interruption | Planned Interruption Equipment
135 |  | 250812O4NRQKBQ | Links F422 |  | Fairlie F380 - Fairlie Rural | 2025-06-12 16:20 | 45820.6806 | 2025-06-12 20:42 | 45820.8625 | 0.02164 | 8.6101e-05 | 3 | 754 | C | DefectiveEquipment | Tx C403 Faulty
136 |  | 26012306KWBOLR | Fuses F422 |  | Fairlie F380 - Fairlie Rural | 2025-06-12 16:20 | 45820.6806 | 2025-06-12 20:42 | 45820.8625 | 0.02164 | 8.6101e-05 | 3 | 754 | C | DefectiveEquipment | Blown Tx C403
137 |  | 250812XDVR9GWE | TO A184 |  | Studholme 07 - Waihaorunga | 2025-06-13 12:41 | 45821.5285 | 2025-06-13 13:02 | 45821.5431 | 0.0012054 | 5.74e-05 | 2 | 42 | C | DefectiveEquipment | open fuse inspect LV connections
138 |  | 250812L4WPRVY9 | Fuses W223 to end |  | Studholme 08 - Mount Studholme | 2025-06-14 16:29 | 45822.6868 | 2025-06-14 17:49 | 45822.7424 | 0.01148 | 0.0001435 | 5 | 400 | C | ThirdPartyInterference | Broken insulator pole
139 |  | 25053013ABMC1N | Albury |  | Fairlie F380 - Fairlie Rural | 2025-06-16 09:00 | 45824.375 | 2025-06-16 12:25 | 45824.5174 | 0.33858 | 0.0018942 | 66 | 11797 | B | Planned interruption | Planned Interruption Equipment
140 |  | 250812UWCN9RSI | Fuses W223 to end |  | Studholme 08 - Mount Studholme | 2025-06-16 13:25 | 45824.559 | 2025-06-16 15:25 | 45824.6424 | 0.01722 | 0.0001435 | 5 | 600 | C | ThirdPartyInterference | Broken disc insulator
141 |  | 250521KD28EUWI | Timaru |  | Timaru 2852 - Hadlow | 2025-06-16 08:40 | 45824.3611 | 2025-06-16 15:59 | 45824.666 | 0.99079 | 0.0023247 | 81 | 34522 | B | Planned interruption | Planned Interruption Equipment
142 |  | 250522BN07FMJB | W238 |  | Studholme 08 - Mount Studholme | 2025-06-17 08:30 | 45825.3542 | 2025-06-17 14:46 | 45825.6153 | 0.1187 | 0.0003157 | 11 | 4136 | B | Planned interruption | Planned Interruption Equipment
143 |  | 2505232M0NGQXP | Bell's Pond |  | Bells Pond CB1 - Waihuna | 2025-06-18 08:30 | 45826.3542 | 2025-06-18 15:54 | 45826.6625 | 0.076457 | 0.0001722 | 6 | 2664 | B | Planned interruption | Planned Interruption Equipment
144 |  | 25060457UOEF8R | Albury |  | Fairlie F380 - Fairlie Rural | 2025-06-19 09:05 | 45827.3785 | 2025-06-19 16:00 | 45827.6667 | 0.38114 | 0.00091841 | 32 | 13280 | B | Planned interruption | Planned Interruption Equipment
145 |  | 2506041H83IMSS | Timaru |  | Pleasant Point CB4 - Totara Valley | 2025-06-23 10:00 | 45831.4167 | 2025-06-23 14:00 | 45831.5833 | 0.06888 | 0.000287 | 10 | 2400 | B | Planned interruption | Planned Interruption Equipment
146 |  | 250609MVEABM8U | W319 |  | Studholme 01 - Otaio | 2025-06-23 09:00 | 45831.375 | 2025-06-23 14:30 | 45831.6042 | 0.18942 | 0.000574 | 20 | 6600 | B | Planned interruption | Planned Interruption Equipment
147 |  | 250609IHP1OKS5 | Albury |  | Fairlie F374 - Cricklewood | 2025-06-24 01:12 | 45832.05 | 2025-06-24 01:20 | 45832.0556 | 0.0050512 | 0.0006314 | 22 | 176 | B | Planned interruption | Planned Interruption Equipment
148 |  | 250521JBYDJTYG | Temuka |  | Temuka 08 - Temuka East | 2025-06-24 07:00 | 45832.2917 | 2025-06-24 07:03 | 45832.2937 | 0.0073185 | 0.0024395 | 85 | 255 | B | Planned interruption | Planned Interruption Equipment
149 |  | 250514XTBUPOTS | Temuka |  | Temuka 08 - Temuka East | 2025-06-24 08:30 | 45832.3542 | 2025-06-24 17:25 | 45832.7257 | 0.81376 | 0.0016072 | 56 | 28354 | B | Planned interruption | Notified Interruption Equipment
150 |  | 250624SWIWXNFJ | D1415 |  | Temuka 03 - Winchester | 2025-06-25 01:19 | 45833.0549 | 2025-06-25 01:20 | 45833.0556 | 0 | 0 | 2 | 2 | B | Planned interruption | Planned Interruption Equipment
151 |  | 250813SVHR7IGD | CB F341 to end |  | Fairlie F380 - Fairlie Rural | 2025-06-25 00:40 | 45833.0278 | 2025-06-25 04:15 | 45833.1771 | 0.51833 | 0.0024108 | 84 | 18060 | C | Wildlife | Tripped on E/F
152 |  | 250813YXEU5SD9 | T121 |  | Temuka 02 - Milford | 2025-06-25 11:03 | 45833.4604 | 2025-06-25 11:15 | 45833.4688 | 0.0024108 | 0.0004879 | 17 | 84 | C | DefectiveEquipment | Low Voltage
153 |  | 250813RJA1AOQY | STU CB2 - ABS W243 - Links W187 |  | Studholme 02 - Glenavy | 2025-06-25 11:31 | 45833.4799 | 2025-06-25 13:54 | 45833.5792 | 0.053354 | 0.0003731 | 13 | 1859 | C | ThirdPartyInterference | Isolation and Earth for Truck removal from pole
154 |  | 250514FNMK5HYN | Temuka |  | Temuka 08 - Temuka East | 2025-06-25 08:30 | 45833.3542 | 2025-06-25 16:42 | 45833.6958 | 0.77097 | 0.0016072 | 56 | 26863 | B | Planned interruption | Notified Interruption Equipment
155 |  | 250813AUXDFXAE | CB F426 (Chamberlain Rd) - Links F166 |  | Albury ABY2742 - Cave | 2025-06-26 01:22 | 45834.0569 | 2025-06-26 10:36 | 45834.4417 | 0.44416 | 0.0014063 | 49 | 15476 | C | VegetationOutZone | Lines brough down by trees
156 |  | 250611AFQSEXWR | B368 |  | Pleasant Point CB4 - Totara Valley | 2025-06-26 09:00 | 45834.375 | 2025-06-26 11:08 | 45834.4639 | 0.0036736 | 2.87e-05 | 1 | 128 | B | Planned interruption | Planned Interruption Equipment
157 |  | 250605WWOLPM5N | Temuka |  | Geraldine G156 - Woodbury | 2025-06-26 08:08 | 45834.3389 | 2025-06-26 16:35 | 45834.691 | 0.12645 | 0.0002583 | 9 | 4406 | B | Planned interruption | Planned Interruption Equipment
158 |  | 250514CYGKXUZW | Temuka |  | Temuka 08 - Temuka East | 2025-06-26 08:30 | 45834.3542 | 2025-06-26 16:47 | 45834.6993 | 0.27426 | 0.000574 | 20 | 9556 | B | Planned interruption | Notified Interruption Equipment
159 |  | 250813NDK7DZPD | L499 |  | Timaru 2952 - Highfield | 2025-06-28 17:40 | 45836.7361 | 2025-06-29 01:00 | 45837.0417 | 0.67365 | 0.0097007 | 338 | 23472 | C | ThirdPartyInterference | Isolate and Earth to replace
160 |  | 250813A6N4GXSB | ABS W221 to end |  | Studholme 08 - Mount Studholme | 2025-06-30 15:17 | 45838.6368 | 2025-06-30 16:03 | 45838.6687 | 0.13483 | 0.0053956 | 188 | 4698 | C | Wildlife | Bird Strike
161 |  | 250514UXQMCOKJ | Temuka |  | Temuka 08 - Temuka East | 2025-07-01 08:00 | 45839.3333 | 2025-07-01 19:05 | 45839.7951 | 2.8808 | 0.0045059 | 157 | 100374 | B | Planned interruption | Notified Interruption Equipment
162 |  | 250613VS4N7KC4 | Timaru |  | Pleasant Point CB4 - Totara Valley | 2025-07-02 09:04 | 45840.3778 | 2025-07-02 13:00 | 45840.5417 | 0.027093 | 0.0001148 | 4 | 944 | B | Planned interruption | Planned Interruption Equipment
163 |  | 250514WGDHGLT3 | Temuka |  | Temuka 08 - Temuka East | 2025-07-02 08:30 | 45840.3542 | 2025-07-02 17:09 | 45840.7146 | 1.0128 | 0.0020377 | 71 | 35290 | B | Planned interruption | Notified Interruption Equipment
164 |  | 2505144X0N1GZF | Temuka |  | Temuka 08 - Temuka East | 2025-07-03 08:30 | 45841.3542 | 2025-07-03 13:05 | 45841.5451 | 0.41314 | 0.0016072 | 56 | 14395 | B | Planned interruption | Notified Interruption Equipment
165 |  | 250521VF4UZGWW | Temuka |  | Temuka 08 - Temuka East | 2025-07-03 17:30 | 45841.7292 | 2025-07-03 17:40 | 45841.7361 | 0.024395 | 0.0024395 | 85 | 850 | B | Planned interruption | Planned Interruption Equipment
166 |  | 2508134K0UHTLU | ABS F313 to ABS T315 and Links T688 |  | Temuka 09 - Waitohi | 2025-07-08 21:53 | 45846.9118 | 2025-07-09 00:34 | 45847.0236 | 0.54358 | 0.004018 | 140 | 18940 | C | DefectiveEquipment | Broken insulator
167 |  | 250813HOM08XIS | ABS F194 to end |  | Fairlie F383 - Fairlie Township | 2025-07-12 08:30 | 45850.3542 | 2025-07-12 13:41 | 45850.5701 | 4.1985 | 0.022817 | 795 | 146287 | C | ThirdPartyInterference | Fire near Pole
168 |  | 250708ZW364U3N | GIS Trace |  | Bells Pond CB1 - Waihuna | 2025-07-14 10:00 | 45852.4167 | 2025-07-14 11:24 | 45852.475 | 0.012054 | 0.0001435 | 5 | 420 | B | Planned interruption | Planned Interruption Equipment
169 |  | 250623HZIXDHVP | Timaru |  | Pleasant Point CB2 - Sutherlands | 2025-07-14 09:05 | 45852.3785 | 2025-07-14 16:10 | 45852.6736 | 0.036019 | 8.6101e-05 | 3 | 1255 | B | Planned interruption | Planned Interruption Equipment
170 |  | 250627ULEBRDLT | GIS Trace |  | Haldon-Lilybank M86 - Haldon-Lilybank | 2025-07-15 10:31 | 45853.4382 | 2025-07-15 12:41 | 45853.5285 | 0.038917 | 0.0007462 | 26 | 1356 | B | Planned interruption | Notified Interruption Equipment
171 |  | 250623VICBLM9W | Timaru |  | Timaru 2952 - Highfield | 2025-07-15 09:00 | 45853.375 | 2025-07-15 12:59 | 45853.541 | 0.6494 | 0.0027265 | 95 | 22627 | B | Planned interruption | Planned Interruption Equipment
172 |  | 250813GZWSGVYC | TO C192 |  | Albury ABY2732 - Raincliff | 2025-07-15 13:21 | 45853.5563 | 2025-07-15 14:38 | 45853.6097 | 0.0022099 | 2.87e-05 | 1 | 77 | C | DefectiveEquipment | Fuse blown
173 |  | 250618E04CO7IN | Temuka |  | Rangitata 03 - Mahan Road | 2025-07-16 08:31 | 45854.3549 | 2025-07-16 15:39 | 45854.6521 | 0.44221 | 0.0010332 | 36 | 15408 | B | Planned interruption | Notified Interruption Equipment
174 |  | 250825ZWVB2DID | W598 |  | Pareora CB4 - St Andrews | 2025-07-17 05:22 | 45855.2236 | 2025-07-17 08:11 | 45855.341 | 0.23767 | 0.0014063 | 49 | 8281 | C | CauseUnknown | Instantaneous Trip
175 |  | 250627VT2HUQGI | GIS Trace |  | Pleasant Point CB1 - Waitawa | 2025-07-17 09:04 | 45855.3778 | 2025-07-17 11:09 | 45855.4646 | 0.04305 | 0.0003444 | 12 | 1500 | B | Planned interruption | Planned Interruption Vegetation
176 |  | 250813JGEURBSX | Fuses TOB1526 |  | Pleasant Point CB5 - Pleasant Point Township | 2025-07-17 11:22 | 45855.4736 | 2025-07-17 11:47 | 45855.491 | 0.0035875 | 0.0001435 | 5 | 125 | C | CauseUnknown | Fuse Blown
177 |  | 250813FKNO6W74 | Tx E10 - LB459cct4 -LB125 - LB123 |  | Tekapo M204 - Lakeside Drive | 2025-07-17 11:02 | 45855.4597 | 2025-07-17 12:20 | 45855.5139 | 0.15894 | 0.0020377 | 71 | 5538 | C | DefectiveEquipment | Oil leak investigation and clean up
178 |  | 250625EVPMZCOL | GIS Trace |  | Pareora CB6 - Normanby | 2025-07-17 09:00 | 45855.375 | 2025-07-17 15:57 | 45855.6646 | 0.11968 | 0.000287 | 10 | 4170 | B | Planned interruption | Vegetation Clearance
179 |  | 250623QN2TGAUF | Timaru |  | Timaru 2952 - Highfield | 2025-07-17 09:00 | 45855.375 | 2025-07-17 16:41 | 45855.6951 | 0.65835 | 0.0014637 | 51 | 22939 | B | Planned interruption | Planned Interruption Equipment
180 |  | 2506276C7Y36BI | GIS Trace |  | Timaru 2742 - Levels Plain | 2025-07-18 09:00 | 45856.375 | 2025-07-18 12:43 | 45856.5299 | 0.28801 | 0.0012915 | 45 | 10035 | B | Planned interruption | Planned Interruption Vegetation
181 |  | 250701KBXKGRA2 | GIS Trace |  | Bells Pond CB2 - Tawai | 2025-07-21 09:28 | 45859.3944 | 2025-07-21 14:33 | 45859.6062 | 0.050684 | 0.0001722 | 6 | 1766 | B | Planned interruption | Planned Interruption Equipment
182 |  | 250630QUIQSDTK | GIS Trace |  | Temuka 01 - Temuka West | 2025-07-21 08:30 | 45859.3542 | 2025-07-21 16:34 | 45859.6903 | 0.83345 | 0.001722 | 60 | 29040 | B | Planned interruption | Notified Interruption Equipment
183 |  | 25070106IHPITI | GIS Trace |  | Timaru 2952 - Highfield | 2025-07-22 11:40 | 45860.4861 | 2025-07-22 14:42 | 45860.6125 | 0.090606 | 0.0005166 | 18 | 3157 | B | Planned interruption | Planned Interruption Equipment
184 |  | 250626ZEAUC0YS | GIS Trace |  | Clandeboye No 1 T613 - Rolleston Road | 2025-07-23 08:32 | 45861.3556 | 2025-07-23 15:50 | 45861.6597 | 0.060127 | 0.0001435 | 5 | 2095 | B | Planned interruption | Planned Interruption Equipment
185 |  | 2506263H0HSFKS | GIS Trace |  | Clandeboye No 1 T613 - Rolleston Road | 2025-07-24 08:30 | 45862.3542 | 2025-07-24 15:43 | 45862.6549 | 0.059696 | 0.0001435 | 5 | 2080 | B | Planned interruption | Planned Interruption Equipment
186 |  | 2506309CJXB07P | GIS Trace |  | Geraldine G194 - Speechley | 2025-07-24 09:00 | 45862.375 | 2025-07-24 15:51 | 45862.6604 | 0.058979 | 0.0001435 | 5 | 2055 | B | Planned interruption | Planned Interruption Equipment
187 |  | 250707XITA2T47 | GIS Trace |  | Temuka 08 - Temuka East | 2025-07-28 08:45 | 45866.3646 | 2025-07-28 18:23 | 45866.766 | 1.8718 | 0.0033866 | 118 | 65218 | B | Planned interruption | Notified Interruption Equipment
188 |  | 250707ZRQAZDN4 | GIS Trace |  | Grasmere Street 02 - White Street | 2025-07-28 19:00 | 45866.7917 | 2025-07-28 20:38 | 45866.8597 | 0.016876 | 0.0001722 | 6 | 588 | B | Planned interruption | Planned Interruption Equipment
189 |  | 2507087AATVUKK | GIS Trace |  | Grasmere Street 02 - White Street | 2025-07-29 10:00 | 45867.4167 | 2025-07-29 15:54 | 45867.6625 | 0.020004 | 5.74e-05 | 2 | 697 | B | Planned interruption | Planned Interruption Equipment
190 |  | 250709KMEEOM30 | GIS Trace |  | Bells Pond CB12 - Ikawai | 2025-07-30 09:00 | 45868.375 | 2025-07-30 11:28 | 45868.4778 | 0.0084953 | 5.74e-05 | 2 | 296 | B | Planned interruption | Planned Interruption Equipment
191 |  | 250711RCWAX20R | GIS Trace |  | Pleasant Point CB4 - Totara Valley | 2025-07-31 09:00 | 45869.375 | 2025-07-31 15:03 | 45869.6271 | 0.041443 | 0.0001148 | 4 | 1444 | B | Planned interruption | Planned Interruption Equipment
192 |  | 250714OSJV8MXC | GIS Trace |  | North Street 08 - Barnard Street | 2025-07-31 22:00 | 45869.9167 | 2025-08-01 06:50 | 45870.2847 | 0.38389 | 0.0008036 | 28 | 13376 | B | Planned interruption | Planned Interruption Equipment
193 |  | 250813WW9C6NYU | W744 |  | Studholme 09 - Morven | 2025-08-03 13:20 | 45872.5556 | 2025-08-03 14:25 | 45872.6007 | 0.007462 | 0.0001148 | 4 | 260 | C | Wildlife | Snow / Bird Strike
194 |  | 2508213AXL3OZZ | TX D552 |  | Temuka 02 - Milford | 2025-08-04 10:55 | 45873.4549 | 2025-08-04 11:46 | 45873.4903 | 0.0014637 | 2.87e-05 | 1 | 51 | C | DefectiveEquipment | Replace LV Pole
195 |  | 250813VC3IBJSY | CB W598 |  | Albury ABY2742 - Cave | 2025-08-05 08:02 | 45874.3347 | 2025-08-05 08:38 | 45874.3597 | 0.0041328 | 0.0001148 | 4 | 144 | C | DefectiveEquipment | 2x Blown DO's
196 |  | 250714ZFOOWXN3 | GIS Trace |  | Temuka 02 - Milford | 2025-08-06 08:38 | 45875.3597 | 2025-08-06 16:50 | 45875.7014 | 0.22547 | 0.0004879 | 17 | 7856 | B | Planned interruption | Notified Interruption Equipment
197 |  | 250807LQZINORS | ABS G116 to end |  | Temuka 03 - Winchester | 2025-08-07 06:50 | 45876.2847 | 2025-08-07 12:32 | 45876.5222 | 0.37993 | 0.0026978 | 94 | 13238 | C | ThirdPartyInterference | Car Vs Pole
198 |  | 250718SKRYBZDY | GIS Trace |  | Grasmere Street 16 - Port Services | 2025-08-07 09:10 | 45876.3819 | 2025-08-07 11:43 | 45876.4882 | 0.0043911 | 2.87e-05 | 1 | 153 | B | Planned interruption | Planned Interruption Equipment
199 |  | 250714IL3AQM92 | GIS Trace |  | Temuka 02 - Milford | 2025-08-07 08:36 | 45876.3583 | 2025-08-07 17:01 | 45876.709 | 0.2317 | 0.0004879 | 17 | 8073 | B | Planned interruption | Notified Interruption Equipment
200 |  | 250724COT7RSNY | GIS Trace |  | Pareora CB6 - Normanby | 2025-08-08 09:00 | 45877.375 | 2025-08-08 10:12 | 45877.425 | 0.0061992 | 8.6101e-05 | 3 | 216 | B | Planned interruption | Planned Interruption Equipment
201 |  | 250723FU3SIF7D | GIS Trace |  | Bells Pond CB12 - Ikawai | 2025-08-08 09:00 | 45877.375 | 2025-08-08 13:45 | 45877.5729 | 0.073616 | 0.0002583 | 9 | 2565 | B | Planned interruption | Planned Interruption Equipment
202 |  | 250814Y8M4LRET | T127 |  | Temuka 07 - Rangitata | 2025-08-09 07:48 | 45878.325 | 2025-08-09 08:46 | 45878.3653 | 0.12318 | 0.0021238 | 74 | 4292 | C | CauseUnknown | Unknown no fault found likely bird strike
203 |  | 250814WFMI6QYB | CB W599 |  | Pareora CB4 - St Andrews | 2025-08-09 15:33 | 45878.6479 | 2025-08-09 16:41 | 45878.6951 | 0.064403 | 0.00094711 | 33 | 2244 | C | Wildlife | Bird found at pole 50422
204 |  | 250714PNMYO966 | GIS Trace |  | Temuka 02 - Milford | 2025-08-11 08:30 | 45880.3542 | 2025-08-11 16:34 | 45880.6903 | 0.122 | 0.0002583 | 9 | 4251 | B | Planned interruption | Notified Interruption Equipment
205 |  | 25081354SYYY7Z | W744 |  | Studholme 09 - Morven | 2025-08-13 10:09 | 45882.4229 | 2025-08-13 11:16 | 45882.4694 | 0.0076916 | 0.0001148 | 4 | 268 | C | Wildlife | Bird Strike
206 |  | 2507254Z8VACAB | GIS Trace |  | Bells Pond CB12 - Ikawai | 2025-08-13 10:03 | 45882.4187 | 2025-08-13 12:05 | 45882.5035 | 0.056023 | 0.0004592 | 16 | 1952 | B | Planned interruption | Planned Interruption Equipment
207 |  | 250725JX8WKIJW | GIS Trace |  | Timaru 2832 - Grants Road | 2025-08-13 09:27 | 45882.3938 | 2025-08-13 12:43 | 45882.5299 | 0.13501 | 0.0006888 | 24 | 4704 | B | Planned interruption | Planned Interruption Equipment
208 |  | 250721WKNKSBC1 | GIS Trace |  | Bells Pond CB2 - Tawai | 2025-08-13 10:00 | 45882.4167 | 2025-08-13 12:43 | 45882.5299 | 0.014034 | 8.6101e-05 | 3 | 489 | B | Planned interruption | Planned Interruption Equipment
209 |  | 250725VCYTPFGB | GIS Trace |  | WSS CB7 Arowhenua and LS1 | 2025-08-13 14:11 | 45882.591 | 2025-08-13 15:24 | 45882.6417 | 0.0062853 | 8.6101e-05 | 3 | 219 | B | Planned interruption | Planned Interruption Equipment
210 |  | 250721SWJ7GGCC | GIS Trace |  | Temuka 07 - Rangitata | 2025-08-14 09:33 | 45883.3979 | 2025-08-14 11:14 | 45883.4681 | 0.020291 | 0.0002009 | 7 | 707 | B | Planned interruption | Planned Interruption Equipment
211 |  | 2507212PFFDRHS | GIS Trace |  | Rangitata 11 - Belfield | 2025-08-14 09:58 | 45883.4153 | 2025-08-14 11:47 | 45883.491 | 0.010275 | 0.0001148 | 4 | 358 | B | Planned interruption | Planned Interruption Equipment
212 |  | 250728PRJG88H9 | GIS Trace |  | Geraldine G156 - Woodbury | 2025-08-14 09:00 | 45883.375 | 2025-08-14 12:00 | 45883.5 | 0.005166 | 2.87e-05 | 1 | 180 | B | Planned interruption | Planned Interruption Equipment
213 |  | 250808WUNAS49D | GIS Trace |  | Hunt Street 05 - Le Cren Street | 2025-08-14 09:00 | 45883.375 | 2025-08-14 13:39 | 45883.5687 | 0.39325 | 0.001435 | 50 | 13702 | B | Planned interruption | Planned Interruption Equipment
214 |  | 250721YZPOS5SS | GIS Trace |  | Rangitata 03 - Mahan Road | 2025-08-14 13:00 | 45883.5417 | 2025-08-14 14:11 | 45883.591 | 0.040754 | 0.000574 | 20 | 1420 | B | Planned interruption | Planned Interruption Equipment
215 |  | 250728SSSYHGGT | GIS Trace |  | Temuka 02 - Milford | 2025-08-18 09:00 | 45887.375 | 2025-08-18 10:30 | 45887.4375 | 0.028413 | 0.0003157 | 11 | 990 | B | Planned interruption | Planned Interruption Vegetation
216 |  | 2508196U6BFHIS | BPD CB1 to end |  | Bells Pond CB12 - Ikawai | 2025-08-18 14:33 | 45887.6062 | 2025-08-18 21:08 | 45887.8806 | 0.23167 | 0.0051947 | 181 | 8072 | C | ThirdPartyInterference | Car Vs Pole
217 |  | 2508197ETFVA51 | TX Fuses TO D1881 |  | Geraldine G156 - Woodbury | 2025-08-18 16:00 | 45887.6667 | 2025-08-18 19:26 | 45887.8097 | 0.0059122 | 2.87e-05 | 1 | 206 | C | Wildlife | Bird Strike
218 |  | 250801SCWWIPRJ | GIS Trace |  | Geraldine G156 - Woodbury | 2025-08-19 09:11 | 45888.3826 | 2025-08-19 15:40 | 45888.6528 | 0.077519 | 0.0002009 | 7 | 2701 | B | Planned interruption | Planned Interruption Equipment
219 |  | 2508013FCOFWTR | GIS Trace |  | Geraldine G156 - Woodbury | 2025-08-21 09:00 | 45890.375 | 2025-08-21 14:12 | 45890.5917 | 0.06139 | 0.0002009 | 7 | 2139 | B | Planned interruption | Planned Interruption Equipment
220 |  | 250825CNP40WPF | Fuses G241 |  | Temuka 03 - Winchester | 2025-08-22 13:01 | 45891.5424 | 2025-08-22 13:42 | 45891.5708 | 0.0070602 | 0.0001722 | 6 | 246 | C | DefectiveEquipment | Repull Stay wire on Pole #08647
221 |  | 250801PK7KBKOF | GIS Trace |  | Studholme 08 - Mount Studholme | 2025-08-22 09:24 | 45891.3917 | 2025-08-22 14:08 | 45891.5889 | 0.065207 | 0.0002296 | 8 | 2272 | B | Planned interruption | Planned Interruption Equipment
222 |  | 250826RRBP479P | W181 |  | Bells Pond CB2 - Tawai | 2025-08-23 07:07 | 45892.2965 | 2025-08-23 09:41 | 45892.4035 | 0.030939 | 0.0002009 | 7 | 1078 | C | Wildlife | Possible Bird strike
223 |  | 250826PQAHI7EZ | CB3 |  | Rangitata 03 - Mahan Road | 2025-08-25 09:31 | 45894.3965 | 2025-08-25 14:49 | 45894.6174 | 0.2098 | 0.004305 | 150 | 7310 | C | DefectiveEquipment | Replace faulty ABS T591
224 |  | 250831ABOOOAKF | CB L636 to LBS L1348 |  | Pareora CB7 - Holmestation | 2025-08-26 14:45 | 45895.6146 | 2025-08-27 12:38 | 45896.5264 | 0.70169 | 0.0059696 | 208 | 24449 | C | ThirdPartyInterference | Truck V lines
225 |  | 250828PLB4CIPR | RMU D14 FS |  | Hunt Street 02 - Wilson Street | 2025-08-26 12:40 | 45895.5278 | 2025-08-26 15:05 | 45895.6285 | 0.12901 | 0.00088971 | 31 | 4495 | C | DefectiveEquipment | Clean TE125 LV panel
226 |  | 250801XEYPH1Z2 | GIS Trace |  | Studholme 03 - Waimate | 2025-08-26 09:08 | 45895.3806 | 2025-08-26 15:49 | 45895.659 | 0.55242 | 0.0013776 | 48 | 19248 | B | Planned interruption | Planned Interruption Equipment
227 |  | 250805VMRAADRB | GIS Trace |  | Studholme 01 - Otaio | 2025-08-27 09:00 | 45896.375 | 2025-08-27 09:49 | 45896.409 | 0.016876 | 0.0003444 | 12 | 588 | B | Planned interruption | Planned Interruption Equipment
228 |  | 250901HPS4RO5S | ABS F117 |  | Geraldine G194 - Speechley | 2025-08-27 10:00 | 45896.4167 | 2025-08-27 11:28 | 45896.4778 | 0.072037 | 0.00086101 | 30 | 2510 | C | DefectiveEquipment | Replace/Repair TX39
229 |  | 2508275VK6PFRW | LV service fuses DOC |  | Unwin Hut M158 - Mt Cook Village Roadside | 2025-08-27 10:00 | 45896.4167 | 2025-08-27 11:34 | 45896.4819 | 0.0078064 | 8.6101e-05 | 3 | 272 | C | CauseUnknown | Move ICP connection @ Tx E179
230 |  | 2508290VTHCETI | ABS W221 |  | Studholme 08 - Mount Studholme | 2025-08-26 14:14 | 45895.5931 | 2025-08-27 12:42 | 45896.5292 | 0.12109 | 0.00086101 | 30 | 4219 | C | DefectiveEquipment | Blown Transformer
231 |  | 250828REODJBQV | TOD507 |  | Geraldine G194 - Speechley | 2025-08-28 06:35 | 45897.2743 | 2025-08-28 07:47 | 45897.3243 | 0.0020664 | 2.87e-05 | 1 | 72 | C | CauseUnknown | Unknown
232 |  | 250806PJQDZEGT | GIS Trace |  | Timaru 2832 - Grants Road | 2025-08-28 10:00 | 45897.4167 | 2025-08-28 11:39 | 45897.4854 | 0.15059 | 0.0015211 | 53 | 5247 | B | Planned interruption | Planned Interruption Equipment
233 |  | 250828PXJIWXJY | TOD1003 |  | Temuka 07 - Rangitata | 2025-08-27 16:47 | 45896.6993 | 2025-08-28 12:07 | 45897.5049 | 0.033292 | 2.87e-05 | 1 | 1160 | C | DefectiveEquipment | Repair broken jumper & DDO's
234 |  | 2508293DUFPMSJ | A1450 |  | Bells Pond CB1 - Waihuna | 2025-06-10 09:27 | 45818.3938 | 2025-08-28 13:02 | 45897.5431 | 3.2711 | 2.87e-05 | 1 | 113975 | B | Planned interruption | Planned Interruption Equipment
235 |  | 250805JOKUNJGB | GIS Trace |  | Clandeboye No 1 T613 - Rolleston Road | 2025-08-28 09:03 | 45897.3771 | 2025-08-28 14:09 | 45897.5896 | 0.017565 | 5.74e-05 | 2 | 612 | B | Planned interruption | Planned Interruption Equipment
236 |  | 250828GQL7JRKZ | Fuses W510 |  | Bells Pond CB12 - Ikawai | 2025-08-28 11:55 | 45897.4965 | 2025-08-28 16:08 | 45897.6722 | 0.06535 | 0.0002583 | 9 | 2277 | C | VegetationInZone | Trees on line
237 |  | 2508071AOFNPOP | GIS Trace |  | Rangitata 11 - Belfield | 2025-09-01 09:10 | 45901.3819 | 2025-09-01 15:47 | 45901.6576 | 0.19436 | 0.0005166 | 18 | 6772 | B | Planned interruption | Planned Interruption Equipment
238 |  | 250911FFOGR9CE | RMU G275 |  | Geraldine G191 - Geraldine Township | 2025-09-01 22:47 | 45901.9493 | 2025-09-02 00:43 | 45902.0299 | 1.5591 | 0.017048 | 594 | 54324 | C | CauseUnknown | Unplanned Trip of RMU G275 CB
239 |  | 250807JFIYZQWR | GIS Trace |  | Rangitata 11 - Belfield | 2025-09-03 09:00 | 45903.375 | 2025-09-03 12:37 | 45903.5257 | 0.10229 | 0.0005166 | 18 | 3564 | B | Planned interruption | Planned Interruption Equipment
240 |  | 250911X9ADTBWY | Milford |  | Temuka 02 - Milford | 2025-09-03 14:02 | 45903.5847 | 2025-09-03 14:36 | 45903.6083 | 0.010734 | 0.0003157 | 11 | 374 | C | DefectiveEquipment | Reposition Insulator on Cross Arm
241 |  | 250815PKPYWCUQ | GIS Trace |  | Pleasant Point CB5 - Pleasant Point Township | 2025-09-05 09:01 | 45905.3757 | 2025-09-05 10:12 | 45905.425 | 0.0020377 | 2.87e-05 | 1 | 71 | B | Planned interruption | Planned Interruption Equipment
242 |  | 250908YACWXTAA | Fuses TOA343 |  | Bells Pond CB13 - Waikakahi | 2025-09-04 20:43 | 45904.8632 | 2025-09-05 10:57 | 45905.4563 | 0.04902 | 5.74e-05 | 2 | 1708 | C | DefectiveEquipment | Blown Fuse TOA343
243 |  | 260203OGCRHE7O | Fuses M53 |  | Tekapo M346 - Unwin Hut 33kV | 2025-09-05 12:43 | 45905.5299 | 2025-09-05 14:17 | 45905.5951 | 0.022673 | 0.0002583 | 9 | 790 | C | DefectiveEquipment | Faulty TX E172
244 |  | 2508148VBHIQC1 | GIS Trace |  | Hunt Street 16 - Arthur Street | 2025-09-07 08:30 | 45907.3542 | 2025-09-07 13:48 | 45907.575 | 0.045346 | 0.0001435 | 5 | 1580 | B | Planned interruption | Planned Interruption Equipment
245 |  | 250818ZRULGPFD | GIS Trace |  | TVS01 - Urban No1 | 2025-09-08 09:00 | 45908.375 | 2025-09-08 13:24 | 45908.5583 | 0.014953 | 5.74e-05 | 2 | 521 | B | Planned interruption | Planned Interruption Equipment
246 |  | 250818VG5S3ZHE | GIS Trace |  | Studholme 09 - Morven | 2025-09-08 08:00 | 45908.3333 | 2025-09-08 15:19 | 45908.6382 | 0.4974 | 0.0011767 | 41 | 17331 | B | Planned interruption | Planned Interruption Equipment
247 |  | 250818HHGDEHWJ | GIS Trace |  | Studholme 09 - Morven | 2025-09-09 08:01 | 45909.334 | 2025-09-09 14:41 | 45909.6118 | 0.14752 | 0.0003731 | 13 | 5140 | B | Planned interruption | Planned Interruption Equipment
248 |  | 250821SOUQWEEV | GIS Trace |  | Timaru 2742 - Levels Plain | 2025-09-10 09:00 | 45910.375 | 2025-09-10 15:54 | 45910.6625 | 0.11882 | 0.000287 | 10 | 4140 | B | Planned interruption | Planned Interruption Vegetation
249 |  | 251002HMASKVHS | 5 Kellands Hill Rd |  | Timaru 2702 - Morgans Road | 2025-09-10 15:19 | 45910.6382 | 2025-09-10 20:45 | 45910.8646 | 3.0034 | 0.032087 | 1118 | 104648 | C | Lightning | Weather - Lightning
250 |  | 250819WM38CSOQ | GIS Trace |  | Temuka 01 - Temuka West | 2025-09-11 09:44 | 45911.4056 | 2025-09-11 14:43 | 45911.6132 | 0.7062 | 0.0024108 | 84 | 24606 | B | Planned interruption | Notified Interruption Equipment
251 |  | 250819RDMPC45Q | GIS Trace |  | Pareora CB4 - St Andrews | 2025-09-11 08:25 | 45911.3507 | 2025-09-11 16:33 | 45911.6896 | 0.014006 | 2.87e-05 | 1 | 488 | B | Planned interruption | Planned Interruption Equipment
252 |  | 251002SLU4BOTZ | 5 Kellans hill Rd |  | Timaru 2702 - Morgans Road | 2025-09-10 15:19 | 45910.6382 | 2025-09-11 18:11 | 45911.7576 | 0.089918 | 8.6101e-05 | 3 | 3133 | C | Lightning | Lightning
253 |  | 2509127AEZPB1G | Fuses T644 |  | Rangitata 02 - Arundel | 2025-09-12 08:44 | 45912.3639 | 2025-09-12 10:49 | 45912.4507 | 0.010763 | 8.6101e-05 | 3 | 375 | C | Lightning | Replace TX D1327 Lightning Arrestors
254 |  | 250819JVXSG6KE | GIS Trace |  | Pareora CB4 - St Andrews | 2025-09-12 09:42 | 45912.4042 | 2025-09-12 13:10 | 45912.5486 | 0.011939 | 5.74e-05 | 2 | 416 | B | Planned interruption | Planned Interruption Equipment
255 |  | 250821VHARSDXB | GIS Trace |  | Timaru 2852 - Hadlow | 2025-09-12 08:00 | 45912.3333 | 2025-09-12 14:21 | 45912.5979 | 0.65609 | 0.001722 | 60 | 22860 | B | Planned interruption | Planned Interruption Equipment
256 |  | 250912KSTHSAQT | CB G295 |  | Geraldine G156 - Woodbury | 2025-09-12 14:05 | 45912.5868 | 2025-09-12 15:22 | 45912.6403 | 0.14143 | 0.0018368 | 64 | 4928 | C | VegetationInZone | CB G295 tripped
257 |  | 250912LR6LTHG5 | TOB1448 |  | Timaru 2852 - Hadlow | 2025-09-12 17:23 | 45912.7243 | 2025-09-12 18:07 | 45912.7549 | 0.0025256 | 5.74e-05 | 2 | 88 | C | VegetationOutZone | Branch on Tx B1448 Bushings
258 |  | 250912CRSDLX9T | F243 |  | Fairlie F374 - Cricklewood | 2025-09-15 03:03 | 45915.1271 | 2025-09-15 03:40 | 45915.1528 | 0.023362 | 0.0006314 | 22 | 814 | B | Planned interruption | Planned Interruption Equipment
259 |  | 250827ID4GHWLH | F122 |  | Pleasant Point CB4 - Totara Valley | 2025-09-15 08:00 | 45915.3333 | 2025-09-15 12:35 | 45915.5243 | 0.14207 | 0.0005166 | 18 | 4950 | B | Planned interruption | Planned Interruption Vegetation
260 |  | 250915UD0EWPBV | Fuses L843 to end |  | Timaru 2852 - Hadlow | 2025-09-15 14:29 | 45915.6035 | 2025-09-15 14:57 | 45915.6229 | 0.0024108 | 8.6101e-05 | 3 | 84 | C | AdverseWeather | Remove Tree Branch
261 |  | 2508254HUTSJ2L | GIS Trace |  | Temuka 02 - Milford | 2025-09-15 08:00 | 45915.3333 | 2025-09-15 15:42 | 45915.6542 | 0.13707 | 0.0003157 | 11 | 4776 | B | Planned interruption | Notified Interruption Equipment
262 |  | 250825KISUHFF3 | GIS Trace |  | Studholme 01 - Otaio | 2025-09-15 08:39 | 45915.3604 | 2025-09-15 15:20 | 45915.6389 | 0.011509 | 2.87e-05 | 1 | 401 | B | Planned interruption | Planned Interruption Equipment
263 |  | 2508253EEZFEPQ | GIS Trace |  | North Street 12 - High Street | 2025-09-15 08:30 | 45915.3542 | 2025-09-15 18:45 | 45915.7812 | 0.27552 | 0.0004592 | 16 | 9600 | B | Planned interruption | Planned Interruption Equipment
264 |  | 250825F355MEKD | GIS Trace |  | Geraldine G191 - Geraldine Township | 2025-09-16 08:37 | 45916.359 | 2025-09-16 14:43 | 45916.6132 | 0.050972 | 0.0001435 | 5 | 1776 | B | Planned interruption | Planned Interruption Equipment
265 |  | 250929J0CK7RA2 | CB W598 |  | Pareora CB4 - St Andrews | 2025-09-16 15:46 | 45916.6569 | 2025-09-16 17:34 | 45916.7319 | 0.11147 | 0.0014063 | 49 | 3884 | C | Wildlife | Line down device flagged lines down
266 |  | 250825VRATTFP5 | GIS Trace |  | Temuka 03 - Winchester | 2025-09-17 09:00 | 45917.375 | 2025-09-17 11:20 | 45917.4722 | 0.04018 | 0.000287 | 10 | 1400 | B | Planned interruption | Planned Interruption Vegetation
267 |  | 250822TNTUPGAV | GIS Trace |  | Bells Pond CB1 - Waihuna | 2025-09-17 08:00 | 45917.3333 | 2025-09-17 15:24 | 45917.6417 | 1.1596 | 0.0026117 | 91 | 40404 | B | Planned interruption | Notified Interruption Equipment
268 |  | 251003Z5QNQKZL | CB G249 - LBS G353 - Fuses T489 |  | Geraldine G156 - Woodbury | 2025-09-17 14:43 | 45917.6132 | 2025-09-17 19:15 | 45917.8021 | 2.1486 | 0.020234 | 705 | 74863 | C | VegetationOutZone | CB G249 trip
269 |  | 251006I2YMT83Z | A549 service |  | Pareora CB4 - St Andrews | 2025-09-17 10:45 | 45917.4479 | 2025-09-17 18:39 | 45917.7771 | 2.2801 | 0.0067732 | 236 | 79445 | C | VegetationInZone | Wind fault
270 |  | 2510065IPM9VGN | ABS F101 to Fuses F173 |  | Albury ABY2742 - Cave | 2025-09-17 10:18 | 45917.4292 | 2025-09-18 12:32 | 45918.5222 | 5.9915 | 0.015211 | 530 | 208763 | C | AdverseWeather | Wind Faults
271 |  | 2509303SFNGXS1 | ABS T667 |  | Temuka 07 - Rangitata | 2025-09-18 05:42 | 45918.2375 | 2025-09-18 07:38 | 45918.3181 | 0.2331 | 0.0021238 | 74 | 8122 | C | CauseUnknown | CB T127 trip on B & C phase OC
272 |  | 251003IQXBMZEB | Fuse T489 to end |  | Geraldine G156 - Woodbury | 2025-09-17 14:43 | 45917.6132 | 2025-09-18 09:11 | 45918.3826 | 0.2544 | 0.0002296 | 8 | 8864 | C | VegetationOutZone | Blown Fuses
273 |  | 2510034KMGKXS2 | ABS T699 to end |  | Geraldine G156 - Woodbury | 2025-09-17 17:37 | 45917.734 | 2025-09-18 11:57 | 45918.4979 | 0.88087 | 0.0008036 | 28 | 30692 | C | VegetationOutZone | Conductors broken
274 |  | 251003BUTVFS3C | Fuses G324 to end |  | Geraldine G156 - Woodbury | 2025-09-17 14:43 | 45917.6132 | 2025-09-18 12:12 | 45918.5083 | 0.29596 | 0.0002296 | 8 | 10312 | C | VegetationOutZone | Broken conductor
275 |  | 251002BFJSNPVV | Transformer - D2044 |  | Temuka 07 - Rangitata | 2025-09-18 09:58 | 45918.4153 | 2025-09-18 12:47 | 45918.5326 | 0.0048503 | 2.87e-05 | 1 | 169 | C | DefectiveEquipment | Replace leaking transformer
276 |  | 250829ETJX7HGA | W482 |  | Studholme 09 - Morven | 2025-09-18 09:05 | 45918.3785 | 2025-09-18 15:58 | 45918.6653 | 0.23706 | 0.000574 | 20 | 8260 | B | Planned interruption | Planned Interruption Vegetation
277 |  | 250822RTHPHAUJ | Trace 1 |  | Timaru 2952 - Highfield | 2025-09-18 09:01 | 45918.3757 | 2025-09-18 16:44 | 45918.6972 | 1.6338 | 0.0036736 | 128 | 56928 | B | Planned interruption | Notified Interruption Equipment
278 |  | 251003DMXZHWCV | ABS W734 to end |  | Studholme 09 - Morven | 2025-09-20 18:11 | 45920.7576 | 2025-09-21 11:01 | 45921.459 | 2.5333 | 0.010246 | 357 | 88268 | C | AdverseWeather | Lines Down
279 |  | 250929IKIYEGHZ | CB G297 |  | Temuka 03 - Winchester | 2025-09-21 05:11 | 45921.216 | 2025-09-21 08:19 | 45921.3465 | 1.8453 | 0.0098155 | 342 | 64296 | C | VegetationOutZone | Wind - branch in line
280 |  | 250929RDSWAKSL | ABS T130 to Links T121 |  | Temuka 07 - Rangitata | 2025-09-21 04:04 | 45921.1694 | 2025-09-21 15:00 | 45921.625 | 2.5844 | 0.0070602 | 246 | 90047 | C | VegetationOutZone | Wind faults
281 |  | 251002G5PR8M23 | Fuses F220 |  | Fairlie F380 - Fairlie Rural | 2025-09-21 06:07 | 45921.2549 | 2025-09-21 09:46 | 45921.4069 | 0.13828 | 0.0006314 | 22 | 4818 | C | CauseUnknown | Blown Fuses
282 |  | 2510298JLBFKNQ | F220 |  | Fairlie F380 - Fairlie Rural | 2025-09-21 06:07 | 45921.2549 | 2025-09-21 09:46 | 45921.4069 | 0.13828 | 0.0006314 | 22 | 4818 | C | CauseUnknown | Blown fuses F220
283 |  | 2510034LQRYMSC | ABS W306 - Fuse W310 - Fuses W311 - Links W349 - Fuses TOA964 - Links at P #48068 |  | Studholme 01 - Otaio | 2025-09-21 04:54 | 45921.2042 | 2025-09-21 17:18 | 45921.7208 | 6.1989 | 0.014178 | 494 | 215988 | C | DefectiveEquipment | Damaged ABS Mechanism
284 |  | 2510022YYSKLGI | Fuses TOA1210 |  | Studholme 09 - Morven | 2025-09-21 12:09 | 45921.5062 | 2025-09-21 17:20 | 45921.7222 | 0.017852 | 5.74e-05 | 2 | 622 | C | CauseUnknown | Blown Fuses
285 |  | 250930OYMCRYTC | ABS T204 |  | Pleasant Point CB1 - Waitawa | 2025-09-23 01:22 | 45923.0569 | 2025-09-23 03:45 | 45923.1562 | 0.81626 | 0.0085527 | 298 | 28441 | C | Wildlife | Possums
286 |  | 250903DOG7VQGD | TX E10 CCT2, CCT3, CCT4 |  | Tekapo M204 - Lakeside Drive | 2025-09-23 08:00 | 45923.3333 | 2025-09-23 13:41 | 45923.5701 | 0.36986 | 0.0021812 | 76 | 12887 | B | Planned interruption | Notified Interruption Equipment
287 |  | 250919SDZXK42I | W151 |  | Bells Pond CB2 - Tawai | 2025-09-23 09:30 | 45923.3958 | 2025-09-23 11:00 | 45923.4583 | 0.43883 | 0.0059983 | 209 | 15290 | B | Planned interruption | Planned Interruption Equipment
288 |  | 251002ACKXTXXP | Fuses L222 |  | Pleasant Point CB4 - Totara Valley | 2025-09-23 10:05 | 45923.4201 | 2025-09-23 10:56 | 45923.4556 | 0.043911 | 0.00086101 | 30 | 1530 | C | DefectiveEquipment | Broken Insulator
289 |  | 250929KTI920IE | Transformer - C38 |  | Albury ABY2742 - Cave | 2025-09-23 13:32 | 45923.5639 | 2025-09-23 14:41 | 45923.6118 | 0.0039606 | 5.74e-05 | 2 | 138 | C | VegetationInZone | Tree fall risk mitigation
290 |  | 250903I7IWPGGB | TX E10 CCT2, CCT3, CCT4 |  | Tekapo M204 - Lakeside Drive | 2025-09-24 08:30 | 45924.3542 | 2025-09-24 14:38 | 45924.6097 | 0.47195 | 0.0013202 | 46 | 16444 | B | Planned interruption | Notified Interruption Equipment
291 |  | 250822JMH6IDDV | Trace 1 |  | Timaru 2952 - Highfield | 2025-09-24 09:00 | 45924.375 | 2025-09-24 17:23 | 45924.7243 | 0.72632 | 0.0015211 | 53 | 25307 | B | Planned interruption | Notified Interruption Equipment
292 |  | 260505JA93DQUF | LB441-21 |  | Timaru 2702 - Morgans Road | 2025-09-24 09:00 | 45924.375 | 2025-09-24 16:58 | 45924.7069 | 0.32925 | 0.0006888 | 24 | 11472 | C | HumanError | Customers missed on planned outage
293 |  | 250925PA3Y5JZF | Fuses TO C288 to end |  | Fairlie F380 - Fairlie Rural | 2025-09-25 06:22 | 45925.2653 | 2025-09-25 12:27 | 45925.5188 | 0.19904 | 0.0005453 | 19 | 6935 | C | DefectiveEquipment | Burnt up '01' LV Main Isolator
294 |  | 250822J8BFDOIP | Trace 1 |  | Timaru 2952 - Highfield | 2025-09-25 09:00 | 45925.375 | 2025-09-25 17:11 | 45925.716 | 0.72508 | 0.0015211 | 53 | 25264 | B | Planned interruption | Notified Interruption Equipment
295 |  | 250924PNNYEC6B | LB441-21 |  | Timaru 2952 - Highfield | 2025-09-25 09:00 | 45925.375 | 2025-09-25 16:52 | 45925.7028 | 0.32512 | 0.0006888 | 24 | 11328 | B | Planned interruption | Planned Interruption Equipment
296 |  | 250822MCDINHSQ | Trace 1 |  | Timaru 2952 - Highfield | 2025-09-26 09:00 | 45926.375 | 2025-09-26 13:36 | 45926.5667 | 1.1145 | 0.0040467 | 141 | 38832 | B | Planned interruption | Notified Interruption Equipment
297 |  | 251001EGRP3Q3Z | ABS F327 minus ABS F393 |  | Albury ABY2742 - Cave | 2025-09-28 15:26 | 45928.6431 | 2025-09-28 17:54 | 45928.7458 | 1.3633 | 0.011882 | 414 | 47500 | C | VegetationOutZone | ABY CB 2742 TRIPPED
298 |  | 251002PJAPFSI8 | CB W499 Tripped |  | Studholme 08 - Mount Studholme | 2025-09-28 21:00 | 45928.875 | 2025-09-28 21:32 | 45928.8972 | 0.14568 | 0.010791 | 376 | 5076 | C | VegetationOutZone | Wind
299 |  | 251001PKRLCLSC | ABS F154 |  | Albury ABY2742 - Cave | 2025-09-29 03:16 | 45929.1361 | 2025-09-29 11:25 | 45929.4757 | 5.0485 | 0.011882 | 414 | 175905 | C | VegetationOutZone | ABY CB 2742 Tripped
300 |  | 250929PQA2MD7X | LVFeeder - A5-01 |  | Pareora CB4 - St Andrews | 2025-09-29 08:24 | 45929.35 | 2025-09-29 10:26 | 45929.4347 | 0.0070028 | 5.74e-05 | 2 | 244 | C | Wildlife | Bird V lines
301 |  | 2509293XCPXEOP | TO D714 |  | Temuka 07 - Rangitata | 2025-09-29 12:10 | 45929.5069 | 2025-09-29 15:56 | 45929.6639 | 0.012972 | 5.74e-05 | 2 | 452 | C | VegetationOutZone | Tree on line
302 |  | 251006VCP2H9MQ | T680 to end |  | Temuka 09 - Waitohi | 2025-09-29 18:13 | 45929.759 | 2025-09-29 21:49 | 45929.909 | 0.086789 | 0.0004018 | 14 | 3024 | C | ThirdPartyInterference | Digger Vs Lines
303 |  | 250925EUSJIAKZ | W648 |  | Pareora CB4 - St Andrews | 2025-09-30 12:02 | 45930.5014 | 2025-09-30 15:32 | 45930.6472 | 0.13259 | 0.0006314 | 22 | 4620 | B | Planned interruption | Planned Interruption Vegetation
304 |  | 2509084YBYHACZ | Tx E178 |  | Unwin Hut M158 - Mt Cook Village Roadside | 2025-09-30 11:20 | 45930.4722 | 2025-09-30 16:00 | 45930.6667 | 0.008036 | 2.87e-05 | 1 | 280 | B | Planned interruption | Planned Interruption Equipment
305 |  | 250908O6R6ONQE | Z210 to Z213 - E4 |  | TVS11 - Urban No2 | 2025-09-30 09:00 | 45930.375 | 2025-09-30 16:32 | 45930.6889 | 1.0678 | 0.0024682 | 86 | 37204 | B | Planned interruption | Notified Interruption Equipment
306 |  | 2509252WSNBAGK | W329 |  | Pareora CB4 - St Andrews | 2025-09-30 09:00 | 45930.375 | 2025-09-30 16:13 | 45930.6757 | 0.26097 | 0.0006027 | 21 | 9093 | B | Planned interruption | Planned Interruption Vegetation
307 |  | 250908RHIBSBCU | B685-03 |  | Timaru 2952 - Highfield | 2025-09-30 09:00 | 45930.375 | 2025-09-30 17:19 | 45930.7215 | 4.1817 | 0.0089258 | 311 | 145704 | B | Planned interruption | Notified Interruption Equipment
308 |  | 251002RDSIS0S9 | ABY CB4242 |  | Fairlie F380 - Fairlie Rural | 2025-10-01 03:50 | 45931.1597 | 2025-10-01 11:17 | 45931.4701 | 9.8783 | 0.022099 | 770 | 344190 | C | DefectiveEquipment | ABY CB4242 tripped due to 33kV Line off Insulator
309 |  | 251002RDSIS0S9 | ABY CB4242 |  | Fairlie F383 - Fairlie Township | 2025-10-01 03:50 | 45931.1597 | 2025-10-01 11:17 | 45931.4701 | 4.5799 | 0.010246 | 357 | 159579 | C | DefectiveEquipment | ABY CB4242 tripped due to 33kV Line off Insulator
310 |  | 251002RDSIS0S9 | ABY CB4242 |  | Fairlie F374 - Cricklewood | 2025-10-01 03:50 | 45931.1597 | 2025-10-01 11:17 | 45931.4701 | 0.66711 | 0.0014924 | 52 | 23244 | C | DefectiveEquipment | ABY CB4242 tripped due to 33kV Line off Insulator
311 |  | 2510060NTZ6UQ3 | TX Fuses TO D1137 |  | Temuka 01 - Temuka West | 2025-10-01 19:09 | 45931.7979 | 2025-10-01 22:03 | 45931.9187 | 0.014981 | 8.6101e-05 | 3 | 522 | C | ThirdPartyInterference | Truck vs lines
312 |  | 250915J5TPBQP2 | Pole 08681 + D243-03 |  | Temuka 03 - Winchester | 2025-10-02 09:00 | 45932.375 | 2025-10-02 16:49 | 45932.7007 | 1.1952 | 0.0026978 | 94 | 41646 | B | Planned interruption | Planned Interruption Equipment
313 |  | 250929L6H5D5OX | F220 |  | Fairlie F380 - Fairlie Rural | 2025-10-03 09:00 | 45933.375 | 2025-10-03 14:23 | 45933.5993 | 0.20394 | 0.0006314 | 22 | 7106 | B | Planned interruption | Planned Interruption Equipment
314 |  | 250910ASBP7WTC | TOC316 |  | Fairlie F380 - Fairlie Rural | 2025-10-03 10:12 | 45933.425 | 2025-10-03 15:07 | 45933.6299 | 0.048618 | 0.0001722 | 6 | 1694 | B | Planned interruption | Planned Interruption Equipment
315 |  | 260203USFYLC4L | LVFeeder - E129-02 |  | Unwin Hut M159 - Mt Cook Village Hillside | 2025-10-03 13:52 | 45933.5778 | 2025-10-03 17:21 | 45933.7229 | 0.14362 | 0.0006888 | 24 | 5004 | C | DefectiveEquipment | Faulty TX bushing
316 |  | 251029OYFTD1GW | F178 |  | Albury ABY2742 - Cave | 2025-10-03 23:11 | 45933.966 | 2025-10-04 13:31 | 45934.5632 | 0.17278 | 0.0002009 | 7 | 6020 | C | DefectiveEquipment | Broken pole 14100
317 |  | 251118JA77E9OS | G129 |  | Geraldine G194 - Speechley | 2025-10-04 14:06 | 45934.5875 | 2025-10-04 21:06 | 45934.8792 | 0.57044 | 0.012542 | 437 | 19876 | C | ThirdPartyInterference | Broken wires Brophy Rd
318 |  | 250916X3JEO4XO | G323 |  | Geraldine G194 - Speechley | 2025-10-06 08:00 | 45936.3333 | 2025-10-06 10:52 | 45936.4528 | 0.19746 | 0.001148 | 40 | 6880 | B | Planned interruption | Planned Interruption Vegetation
319 |  | 251029INR9SNIC | ABS W151 to ABS W174 |  | Bells Pond CB2 - Tawai | 2025-10-06 11:13 | 45936.4674 | 2025-10-06 13:25 | 45936.559 | 0.59937 | 0.0075768 | 264 | 20884 | C | ThirdPartyInterference | Fencing wire on lines
320 |  | 250917EXPCPDWW | ABS W199 |  | Studholme 02 - Glenavy | 2025-10-06 10:27 | 45936.4354 | 2025-10-06 13:26 | 45936.5597 | 0.0051373 | 2.87e-05 | 1 | 179 | B | Planned interruption | Planned Interruption Equipment
321 |  | 250917Q7RAMFNA | G136 |  | Geraldine G194 - Speechley | 2025-10-07 09:00 | 45937.375 | 2025-10-07 11:30 | 45937.4792 | 0.15068 | 0.0010045 | 35 | 5250 | B | Planned interruption | Planned Interruption Vegetation
322 |  | 250916LVVPRW2U | Pole 08511 |  | Temuka 03 - Winchester | 2025-10-07 09:00 | 45937.375 | 2025-10-07 12:02 | 45937.5014 | 0.026117 | 0.0001435 | 5 | 910 | B | Planned interruption | Planned Interruption Vegetation
323 |  | 2509157LR578OT | Z139 |  | Twizel TVS02 - Glen Lyon | 2025-10-07 08:31 | 45937.3549 | 2025-10-07 13:11 | 45937.5493 | 0.056252 | 0.0002009 | 7 | 1960 | B | Planned interruption | Planned Interruption Equipment
324 |  | 250916RV4P5ALB | TE114-16 |  | Hunt Street 05 - Le Cren Street | 2025-10-07 09:00 | 45937.375 | 2025-10-07 14:53 | 45937.6201 | 0.010131 | 2.87e-05 | 1 | 353 | B | Planned interruption | Planned Interruption Equipment
325 |  | 250917ZAWV0BWY | T332+T318 |  | Temuka 09 - Waitohi | 2025-10-08 09:00 | 45938.375 | 2025-10-08 11:06 | 45938.4625 | 0.16273 | 0.0012915 | 45 | 5670 | B | Planned interruption | Planned Interruption Vegetation
326 |  | 2509155Z5XVZNR | T120+Pole 03845 |  | Temuka 02 - Milford | 2025-10-08 08:00 | 45938.3333 | 2025-10-08 17:48 | 45938.7417 | 1.9404 | 0.0034153 | 119 | 67611 | B | Planned interruption | Notified Interruption Equipment
327 |  | 250915FX2NBVS6 | LB C146-29 + LB C10-02 |  | North Street 11 - Hayes Street | 2025-10-08 22:01 | 45938.9174 | 2025-10-09 06:09 | 45939.2562 | 0.18819 | 0.0004018 | 14 | 6557 | B | Planned interruption | Planned Interruption Equipment
328 |  | 250912FFKEWDLB | L539-L504-B1422-04 |  | Timaru 2702 - Morgans Road | 2025-10-09 09:00 | 45939.375 | 2025-10-09 14:25 | 45939.6007 | 0.17722 | 0.0005453 | 19 | 6175 | B | Planned interruption | Planned Interruption Equipment
329 |  | 251017HXOJNWTJ | TX A1513-3 |  | Studholme 07 - Waihaorunga | 2025-10-09 08:51 | 45939.3688 | 2025-10-09 15:00 | 45939.625 | 0.11649 | 0.0003157 | 11 | 4059 | C | ThirdPartyInterference | Replace DB4151 after vehicle hitting it
330 |  | 251029QAUPCQUK | G116 |  | Temuka 03 - Winchester | 2025-10-10 06:33 | 45940.2729 | 2025-10-10 10:30 | 45940.4375 | 0.47063 | 0.0036449 | 127 | 16398 | C | DefectiveEquipment | Broken conductor
331 |  | 251029UX34JMX1 | GLD CB156 |  | Geraldine G191 - Geraldine Township | 2025-10-10 11:51 | 45940.4938 | 2025-10-10 12:04 | 45940.5028 | 0.8462 | 0.065092 | 2268 | 29484 | C | HumanError | GLD Cb191 CB156 Trip
332 |  | 2509198JYUSVPG | TOA572 |  | Studholme 01 - Otaio | 2025-10-10 09:00 | 45940.375 | 2025-10-10 14:22 | 45940.5986 | 0.018483 | 5.74e-05 | 2 | 644 | B | Planned interruption | Planned Interruption Vegetation
333 |  | 251011KKJELTDY | CB M86 |  | Haldon-Lilybank M86 - Haldon-Lilybank | 2025-10-11 10:08 | 45941.4222 | 2025-10-11 16:33 | 45941.6896 | 0.14562 | 0.0023534 | 82 | 5074 | C | DefectiveEquipment | Tipped X-arm & lines down Lilybank Rd
334 |  | 250926NGUNNPPZ | LX71 |  | Grasmere Street 10 - Ashbury Park | 2025-10-11 09:00 | 45941.375 | 2025-10-11 13:28 | 45941.5611 | 0.084608 | 0.0003157 | 11 | 2948 | B | Planned interruption | Planned Interruption Equipment
335 |  | 251029RL35CD0P | Transformer - C76 |  | Fairlie F374 - Cricklewood | 2025-10-13 04:48 | 45943.2 | 2025-10-13 10:40 | 45943.4444 | 0.060615 | 0.0001722 | 6 | 2112 | C | AdverseWeather | Wind
336 |  | 250919AKWPO8DC | L253 |  | Pleasant Point CB4 - Totara Valley | 2025-10-13 09:03 | 45943.3771 | 2025-10-13 12:05 | 45943.5035 | 0.099245 | 0.0005453 | 19 | 3458 | B | Planned interruption | Planned Interruption Vegetation
337 |  | 260203WA8QCYE2 | Fuses Z427 |  | Twizel TVS03 - Pukaki | 2025-10-13 08:11 | 45943.341 | 2025-10-13 12:55 | 45943.5382 | 0.11411 | 0.0004018 | 14 | 3976 | C | DefectiveEquipment | Broken Pole #18413
338 |  | 250915KO6ICGZR | TE81-01 |  | Grasmere Street 20 - Hobbs Street | 2025-10-13 08:30 | 45943.3542 | 2025-10-13 18:32 | 45943.7722 | 2.1719 | 0.0039032 | 136 | 75677 | B | Planned interruption | Notified Interruption Equipment
339 |  | 251010KTKDRUZY | ABS T130 to temp links Pole #01744 |  | Temuka 02 - Milford | 2025-10-14 07:43 | 45944.3215 | 2025-10-14 16:32 | 45944.6889 | 0.0006888 | 0.0003444 | 24 | 36 | B | Planned interruption | Planned Interruption Equipment
340 |  | 250915UUF3UAH4 | Pole 01744 |  | Temuka 02 - Milford | 2025-10-14 08:00 | 45944.3333 | 2025-10-14 13:33 | 45944.5646 | 0.056884 | 0.0001722 | 6 | 1982 | B | Planned interruption | Notified Interruption Equipment
341 |  | 250919LSXGSJBH | L842 |  | Timaru 2852 - Hadlow | 2025-10-14 08:57 | 45944.3729 | 2025-10-14 14:53 | 45944.6201 | 0.020435 | 5.74e-05 | 2 | 712 | B | Planned interruption | Planned Interruption Equipment
342 |  | 250915SA9X8ARS | TE81-11 + TE81-12 + TE81-14 + TE81-15 + TE81-16 + TE81-18 |  | Grasmere Street 20 - Hobbs Street | 2025-10-14 08:32 | 45944.3556 | 2025-10-14 15:48 | 45944.6583 | 1.2202 | 0.0029561 | 103 | 42515 | B | Planned interruption | Notified Interruption Equipment
343 |  | 251003EHV6AQUR | F243 |  | Fairlie F374 - Cricklewood | 2025-10-14 21:30 | 45944.8958 | 2025-10-14 21:57 | 45944.9146 | 0.017048 | 0.0006314 | 22 | 594 | B | Planned interruption | Planned Interruption Equipment
344 |  | 251010MQSNOUX6 | ABS T130 to temp links Pole #01744 |  | Temuka 02 - Milford | 2025-10-15 07:59 | 45945.3326 | 2025-10-15 16:36 | 45945.6917 | 0.003444 | 0.0006888 | 24 | 120 | B | Planned interruption | Planned Interruption Equipment
345 |  | 250925IRRWW7P5 | L879 |  | WSS CB7 Arowhenua and LS1 | 2025-10-15 09:00 | 45945.375 | 2025-10-15 10:37 | 45945.4424 | 0.030623 | 0.0003157 | 11 | 1067 | B | Planned interruption | Planned Interruption Vegetation
346 |  | 250923HRHIWAI0 | T323 |  | Geraldine G194 - Speechley | 2025-10-15 09:00 | 45945.375 | 2025-10-15 13:33 | 45945.5646 | 0.0078351 | 2.87e-05 | 1 | 273 | B | Planned interruption | Planned Interruption Vegetation
347 |  | 2509230FR8SSDB | G108 |  | Temuka 03 - Winchester | 2025-10-15 09:07 | 45945.3799 | 2025-10-15 14:23 | 45945.5993 | 0.30835 | 0.00097581 | 34 | 10744 | B | Planned interruption | Planned Interruption Equipment
348 |  | 250915BSNIL1VS | TE81-11+TE81-12+TE81-16+TE81-18 |  | Grasmere Street 20 - Hobbs Street | 2025-10-15 08:31 | 45945.3549 | 2025-10-15 15:49 | 45945.659 | 0.64911 | 0.0015498 | 54 | 22617 | B | Planned interruption | Notified Interruption Equipment
349 |  | 250925JLZCTZN6 | L309 |  | WSS CB11 Waipopo | 2025-10-15 12:00 | 45945.5 | 2025-10-15 15:28 | 45945.6444 | 1.3605 | 0.0066297 | 231 | 47404 | B | Planned interruption | Planned Interruption Vegetation
350 |  | 250925OHKLHPVS | M21 |  | Haldon-Lilybank M86 - Haldon-Lilybank | 2025-10-15 08:30 | 45945.3542 | 2025-10-15 16:31 | 45945.6882 | 0.02761 | 5.74e-05 | 2 | 962 | B | Planned interruption | Planned Interruption Vegetation
351 |  | 250915JZVBGR4F | Pole 01744 |  | Temuka 02 - Milford | 2025-10-15 08:02 | 45945.3347 | 2025-10-15 16:34 | 45945.6903 | 0.088167 | 0.0001722 | 6 | 3072 | B | Planned interruption | Notified Interruption Equipment
352 |  | 251017EWUDQJFL | Fuses L227 to end |  | Pleasant Point CB2 - Sutherlands | 2025-10-16 08:25 | 45946.3507 | 2025-10-16 11:12 | 45946.4667 | 0.091066 | 0.0005453 | 19 | 3173 | C | ThirdPartyInterference | Digger VS Lines
353 |  | 260203MZFXJ9DM | Transformer - B1485 |  | Pleasant Point CB1 - Waitawa | 2025-10-16 11:40 | 45946.4861 | 2025-10-16 12:03 | 45946.5021 | 0.0039606 | 0.0001722 | 6 | 138 | C | CauseUnknown | Unknown
354 |  | 2509157WQW0W7N | T106 |  | Temuka 02 - Milford | 2025-10-16 08:00 | 45946.3333 | 2025-10-16 14:54 | 45946.6208 | 0.011882 | 2.87e-05 | 1 | 414 | B | Planned interruption | Notified Interruption Equipment
355 |  | 251017ILP571GM | ABS W494 to end |  | Bells Pond CB2 - Tawai | 2025-10-16 14:11 | 45946.591 | 2025-10-16 16:27 | 45946.6854 | 0.80794 | 0.0075768 | 264 | 28151 | C | CauseUnknown | Unknown
356 |  | 250925ZLWLDIXQ | TE82-01 |  | North Street 05 - Cragie Avenue | 2025-10-16 09:02 | 45946.3764 | 2025-10-16 16:00 | 45946.6667 | 1.2239 | 0.0030709 | 107 | 42644 | B | Planned interruption | Notified Interruption Equipment
357 |  | 251017WAMNM0Z6 | Fuses W521 to end |  | Bells Pond CB13 - Waikakahi | 2025-10-16 14:15 | 45946.5938 | 2025-10-16 16:59 | 45946.7076 | 0.051775 | 0.0003157 | 11 | 1804 | C | DefectiveEquipment | Tipped up crossarm
358 |  | 251017KX5UTHEB | Fuses F257 to end |  | Fairlie F380 - Fairlie Rural | 2025-10-17 09:56 | 45947.4139 | 2025-10-17 10:28 | 45947.4361 | 0.0055104 | 0.0001722 | 6 | 192 | C | DefectiveEquipment | Conductor re-bind
359 |  | 250925PS9XU3IR | L227 |  | Pleasant Point CB2 - Sutherlands | 2025-10-17 09:00 | 45947.375 | 2025-10-17 14:35 | 45947.6076 | 0.17306 | 0.0005166 | 18 | 6030 | B | Planned interruption | Planned Interruption Equipment
360 |  | 250925ANHKYIJB | W569 |  | Studholme 09 - Morven | 2025-10-17 08:30 | 45947.3542 | 2025-10-17 14:53 | 45947.6201 | 0.46687 | 0.0012628 | 44 | 16267 | B | Planned interruption | Planned Interruption Equipment
361 |  | 250929GBYLADMO | L331-L754-B1986 |  | WSS CB11 Waipopo | 2025-10-18 08:30 | 45948.3542 | 2025-10-18 15:38 | 45948.6514 | 0.37218 | 0.00088971 | 31 | 12968 | B | Planned interruption | Planned Interruption Equipment
362 |  | 250929QTG5GMPJ | TOA964 |  | Studholme 01 - Otaio | 2025-10-20 09:00 | 45950.375 | 2025-10-20 13:01 | 45950.5424 | 0.0069167 | 2.87e-05 | 1 | 241 | B | Planned interruption | Planned Interruption Equipment
363 |  | 251002LGERSQLP | W337 |  | Pareora CB4 - St Andrews | 2025-10-20 08:00 | 45950.3333 | 2025-10-20 14:41 | 45950.6118 | 0.58695 | 0.0014637 | 51 | 20451 | B | Planned interruption | Planned Interruption Equipment
364 |  | 251029QS3NAXGG | T634 |  | Temuka 08 - Temuka East | 2025-10-20 14:16 | 45950.5944 | 2025-10-20 15:07 | 45950.6299 | 0.12295 | 0.0024108 | 84 | 4284 | C | VegetationInZone | Branch on line
365 |  | 251029I8E5QK4P | L1330 |  | Pareora CB7 - Holmestation | 2025-10-20 15:13 | 45950.634 | 2025-10-20 21:23 | 45950.891 | 0.96051 | 0.0066871 | 233 | 33467 | C | VegetationInZone | broken poles from tree v lines
366 |  | 251029JW9KCBLS | ABS W216 |  | Studholme 08 - Mount Studholme | 2025-10-20 14:25 | 45950.6007 | 2025-10-20 16:34 | 45950.6903 | 0.64785 | 0.0054243 | 189 | 22573 | C | VegetationInZone | Branches V Lines
367 |  | 251029VEP8LUBV | L115 |  | Pareora CB4 - St Andrews | 2025-10-20 15:52 | 45950.6611 | 2025-10-20 16:35 | 45950.691 | 0.038257 | 0.00088971 | 31 | 1333 | C | VegetationInZone | Branch on line
368 |  | 2509302FUZCXFO | ABS F226 |  | Fairlie F380 - Fairlie Rural | 2025-10-20 10:00 | 45950.4167 | 2025-10-20 17:34 | 45950.7319 | 0.14333 | 0.0003157 | 11 | 4994 | B | Planned interruption | Planned Interruption Equipment
369 |  | 251029PSSAXLQ6 | 33kV F400 |  | Fairlie F380 - Fairlie Rural | 2025-10-20 13:53 | 45950.5785 | 2025-10-20 20:55 | 45950.8715 | 1.7364 | 0.0073185 | 255 | 60501 | C | VegetationInZone | tree v lines
370 |  | 251103ZWHTBZWE | ABS FX14 + Highlighted ICPs |  | Albury ABY2732 - Raincliff | 2025-10-20 11:01 | 45950.459 | 2025-10-20 20:40 | 45950.8611 | 0.12935 | 0.00094711 | 33 | 4507 | C | Lightning | Defective Transformer
371 |  | 251103J8KBQROB | F175 |  | Albury ABY2742 - Cave | 2025-10-20 12:58 | 45950.5403 | 2025-10-20 21:16 | 45950.8861 | 0.085756 | 0.0001722 | 6 | 2988 | C | DefectiveEquipment | Broken Poles #51256 & #13891
372 |  | 251029XNLGNRJ1 | W330 |  | Pareora CB4 - St Andrews | 2025-10-20 18:58 | 45950.7903 | 2025-10-20 21:50 | 45950.9097 | 0.049364 | 0.000287 | 10 | 1720 | C | DefectiveEquipment | unknown
373 |  | 251103SODSDGD5 | Fuses L226 |  | Pleasant Point CB2 - Sutherlands | 2025-10-20 20:35 | 45950.8576 | 2025-10-21 09:36 | 45951.4 | 0.20173 | 0.0002583 | 9 | 7029 | C | DefectiveEquipment | Lines Down
374 |  | 251003KDGH00HZ | TE163-13 |  | Grasmere Street 07 - Douglas Street | 2025-10-21 09:13 | 45951.384 | 2025-10-21 15:06 | 45951.6292 | 0.050656 | 0.0001435 | 5 | 1765 | B | Planned interruption | Planned Interruption Equipment
375 |  | 2510295YFRTEUY | ABS T224 to end |  | Temuka 08 - Temuka East | 2025-10-21 15:33 | 45951.6479 | 2025-10-21 21:45 | 45951.9062 | 10.2028 | 0.062279 | 2170 | 355495 | C | VegetationOutZone | TMK CB 8 Trip
376 |  | 251103SJAUIYWY | Fuses F175 - P #13881 |  | Albury ABY2742 - Cave | 2025-10-20 12:58 | 45950.5403 | 2025-10-21 16:40 | 45951.6944 | 0.81658 | 0.0006601 | 23 | 28452 | C | DefectiveEquipment | 11kv Lines Down
377 |  | 251029IWPXGSZN | T108 |  | Temuka 02 - Milford | 2025-10-21 15:28 | 45951.6444 | 2025-10-21 21:05 | 45951.8785 | 0.10639 | 0.0003157 | 11 | 3707 | C | VegetationInZone | branch v lines
378 |  | 251014T6PGLPOK | F243 |  | Fairlie F374 - Cricklewood | 2025-10-21 04:09 | 45951.1729 | 2025-10-22 04:29 | 45952.1868 | 0.92185 | 0.0006314 | 22 | 32120 | B | Planned interruption | Planned Interruption Equipment
379 |  | 251104HBIGHBJ4 | Transformer - E265 |  | Twizel TVS02 - Glen Lyon | 2025-10-22 08:43 | 45952.3632 | 2025-10-22 14:08 | 45952.5889 | 0.1402 | 0.0005453 | 19 | 4885 | C | VegetationInZone | Tree branch beyond Z105
380 |  | 251029MJ3BEDBV | GRM CB2 to RMU L4 |  | Grasmere Street 02 - White Street | 2025-10-22 15:32 | 45952.6472 | 2025-10-22 16:38 | 45952.6931 | 0.65643 | 0.010676 | 372 | 22872 | C | ThirdPartyInterference | Cable fault Te Weka Street
381 |  | 251029J4VSDCWK | ABS M212 |  | Tekapo M201 - Simons Pass | 2025-10-23 10:22 | 45953.4319 | 2025-10-24 14:02 | 45954.5847 | 0.26858 | 0.0016359 | 57 | 9358 | C | ThirdPartyInterference | 3rd party cable fault
382 |  | 251029QJLPY3UX | T489 |  | Geraldine G156 - Woodbury | 2025-10-23 10:12 | 45953.425 | 2025-10-23 13:42 | 45953.5708 | 0.048216 | 0.0002296 | 8 | 1680 | C | DefectiveEquipment | Wind
383 |  | 251029HNMJXS0C | TOD171 |  | Temuka 03 - Winchester | 2025-10-23 09:35 | 45953.3993 | 2025-10-23 19:34 | 45953.8153 | 0.034383 | 5.74e-05 | 2 | 1198 | C | DefectiveEquipment | Blown Customer Switchboard
384 |  | 251029XG07HHAY | W334 |  | Pareora CB7 - Holmestation | 2025-10-23 15:04 | 45953.6278 | 2025-10-23 20:40 | 45953.8611 | 0.019287 | 5.74e-05 | 2 | 672 | C | CauseUnknown | Unknown
385 |  | 251029JWMCVD7D | Transformer - D1081 |  | Geraldine G194 - Speechley | 2025-10-23 16:20 | 45953.6806 | 2025-10-23 20:40 | 45953.8611 | 0.014924 | 5.74e-05 | 2 | 520 | C | Lightning | Blown TX
386 |  | 251029C3BWBNLW | T645 |  | Temuka 07 - Rangitata | 2025-10-23 15:20 | 45953.6389 | 2025-10-23 21:39 | 45953.9021 | 0.23098 | 0.0006601 | 23 | 8048 | C | DefectiveEquipment | broken jumper
387 |  | 251031CB4HJUCX | Fuses M355to end |  | Tekapo M346 - Unwin Hut 33kV | 2025-10-23 09:00 | 45953.375 | 2025-10-24 11:57 | 45954.4979 | 0.27845 | 0.0001722 | 6 | 9702 | C | Lightning | Lines Down
388 |  | 251029AIYPW29T | E172 |  | Tekapo M346 - Unwin Hut 33kV | 2025-10-23 09:00 | 45953.375 | 2025-10-24 12:52 | 45954.5361 | 0.2521 | 0.0002583 | 9 | 8784 | C | Lightning | Blown TX E172
389 |  | 251007EYANAFQV | TOD1085 |  | Temuka 03 - Winchester | 2025-10-24 09:35 | 45954.3993 | 2025-10-24 15:40 | 45954.6528 | 0.020951 | 5.74e-05 | 2 | 730 | B | Planned interruption | Planned Interruption Equipment
390 |  | 251029SCWVVZP2 | KCK738 |  | Albury ABY2732 - Raincliff | 2025-10-25 10:30 | 45955.4375 | 2025-10-25 17:25 | 45955.7257 | 0.011911 | 2.87e-05 | 1 | 415 | C | DefectiveEquipment | Faulty Tx
391 |  | 251118RKYMNROM | ABY CB2742 - F393 & F154 |  | Albury ABY2742 - Cave | 2025-10-26 01:35 | 45956.066 | 2025-10-26 07:33 | 45956.3146 | 3.9499 | 0.011882 | 414 | 137625 | C | CauseUnknown | Cave ABY CB2742 Trip E/F
392 |  | 251029TTFGJXBP | Z102 |  | Twizel TVS02 - Glen Lyon | 2025-10-27 21:13 | 45957.884 | 2025-10-27 23:44 | 45957.9889 | 0.060816 | 0.0005453 | 19 | 2119 | C | VegetationInZone | Branch on line pole 18349
393 |  | 251001ZDIYQTQ6 | F453 to F122 |  | Pleasant Point CB4 - Totara Valley | 2025-10-28 09:00 | 45958.375 | 2025-10-28 13:55 | 45958.5799 | 0.63189 | 0.0032431 | 113 | 22017 | B | Planned interruption | Notified Interruption Equipment
394 |  | 251010WUKPQWPM | B270 |  | Timaru 2742 - Levels Plain | 2025-10-29 09:00 | 45959.375 | 2025-10-29 10:56 | 45959.4556 | 0.016646 | 0.0001435 | 5 | 580 | B | Planned interruption | Planned Interruption Vegetation
395 |  | 251015ZEVK91S1 | TX B878-02 |  | Timaru 2832 - Grants Road | 2025-10-29 09:43 | 45959.4049 | 2025-10-29 14:14 | 45959.5931 | 0.054444 | 0.0002009 | 7 | 1897 | B | Planned interruption | Planned Interruption Equipment
396 |  | 251007USGX1U1O | ABS T224 to Pole #30365 |  | Temuka 08 - Temuka East | 2025-10-29 08:00 | 45959.3333 | 2025-10-29 14:25 | 45959.6007 | 2.1543 | 0.0056539 | 197 | 75061 | B | Planned interruption | Notified Interruption Equipment
397 |  | 251010QD6VMOJP | TE71+TE21+TE1 |  | Hunt Street 16 - Arthur Street | 2025-10-29 18:00 | 45959.75 | 2025-10-29 18:51 | 45959.7854 | 0.074649 | 0.0014637 | 51 | 2601 | B | Planned interruption | Planned Interruption Equipment
398 |  | 251009RVZTICFQ | TOC552 |  | Fairlie F380 - Fairlie Rural | 2025-10-30 09:27 | 45960.3938 | 2025-10-30 12:12 | 45960.5083 | 0.028413 | 0.0001722 | 6 | 990 | B | Planned interruption | Planned Interruption Equipment
399 |  | 251013UAKPOPIM | L843 |  | Timaru 2852 - Hadlow | 2025-10-30 08:01 | 45960.334 | 2025-10-30 16:00 | 45960.6667 | 0.17872 | 0.0003731 | 13 | 6227 | B | Planned interruption | Planned Interruption Equipment
400 |  | 251009CLHBCHRJ | TOB1071 |  | WSS CB5 Washdyke | 2025-10-31 09:00 | 45961.375 | 2025-10-31 13:09 | 45961.5479 | 0.021439 | 8.6101e-05 | 3 | 747 | B | Planned interruption | Planned Interruption Equipment
401 |  | 251015H7PSF4VC | TOB1560 |  | WSS CB11 Waipopo | 2025-10-31 09:00 | 45961.375 | 2025-10-31 13:36 | 45961.5667 | 0.015842 | 5.74e-05 | 2 | 552 | B | Planned interruption | Planned Interruption Equipment
402 |  | 251101SVZEWROY | Fuses L122 |  | Pareora CB7 - Holmestation | 2025-11-01 02:05 | 45962.0868 | 2025-11-01 06:42 | 45962.2792 | 0.11925 | 0.0004305 | 15 | 4155 | C | CauseUnknown | Unknown
403 |  | 251106HM2BT8VU | STU CB2 to W125 & W723 |  | Studholme 02 - Glenavy | 2025-11-01 05:34 | 45962.2319 | 2025-11-01 14:14 | 45962.5931 | 1.2559 | 0.015182 | 529 | 43758 | C | DefectiveEquipment | Broken Wire
404 |  | 251010TNZCLCAB | TE146 |  | North Street 10 - Fraser Street | 2025-11-01 09:26 | 45962.3931 | 2025-11-01 15:24 | 45962.6417 | 0.020521 | 5.74e-05 | 2 | 715 | B | Planned interruption | Planned Interruption Equipment
405 |  | 251102KI9XHCNG | TO A209 |  | Studholme 09 - Morven | 2025-11-02 05:23 | 45963.2243 | 2025-11-02 06:27 | 45963.2688 | 0.0018368 | 2.87e-05 | 1 | 64 | C | Wildlife | Possum
406 |  | 251007ASKPFU3N | D779-01 towards Pole #30350 |  | Temuka 08 - Temuka East | 2025-11-03 09:02 | 45964.3764 | 2025-11-03 16:14 | 45964.6764 | 0.32236 | 0.0007462 | 26 | 11232 | B | Planned interruption | Notified Interruption Equipment
407 |  | 2511067OEDF2OJ | Fuses F428 |  | Albury ABY2742 - Cave | 2025-11-05 10:01 | 45966.4174 | 2025-11-05 12:02 | 45966.5014 | 0.093763 | 0.0007749 | 27 | 3267 | C | DefectiveEquipment | Emergency Replace 11kV X arm
408 |  | 250911RAKSZDWZ | F322 |  | Fairlie F380 - Fairlie Rural | 2025-11-05 09:08 | 45966.3806 | 2025-11-05 16:07 | 45966.6715 | 0.070574 | 0.0001722 | 6 | 2459 | B | Planned interruption | Planned Interruption Vegetation
409 |  | 251010ZC7OFIIQ | TOD152 |  | Temuka 03 - Winchester | 2025-11-06 09:11 | 45967.3826 | 2025-11-06 14:30 | 45967.6042 | 0.0091554 | 2.87e-05 | 1 | 319 | B | Planned interruption | Planned Interruption Equipment
410 |  | 251109T9JAKPXC | CB F380 (FLE Rural) |  | Fairlie F380 - Fairlie Rural | 2025-11-09 14:36 | 45970.6083 | 2025-11-09 17:24 | 45970.725 | 3.7753 | 0.022472 | 783 | 131544 | C | CauseUnknown | ABY CB4242 Trip
411 |  | 251109T9JAKPXC | CB F380 (FLE Rural) |  | Fairlie F383 - Fairlie Township | 2025-11-09 14:36 | 45970.6083 | 2025-11-09 17:26 | 45970.7264 | 1.7418 | 0.010246 | 357 | 60690 | C | CauseUnknown | ABY CB4242 Trip
412 |  | 251109T9JAKPXC | CB F380 (FLE Rural) |  | Fairlie F374 - Cricklewood | 2025-11-09 14:36 | 45970.6083 | 2025-11-09 17:27 | 45970.7271 | 0.2552 | 0.0014924 | 52 | 8892 | C | CauseUnknown | ABY CB4242 Trip
413 |  | 251016AX5A1HW4 | TOB1322 |  | Pareora CB4 - St Andrews | 2025-11-10 08:30 | 45971.3542 | 2025-11-10 11:20 | 45971.4722 | 0.004879 | 2.87e-05 | 1 | 170 | B | Planned interruption | Planned Interruption Equipment
414 |  | 251010ZUBVLPBM | TOD1504 |  | Rangitata 13 - Rangitata Island | 2025-11-10 09:16 | 45971.3861 | 2025-11-10 11:35 | 45971.4826 | 0.0039893 | 2.87e-05 | 1 | 139 | B | Planned interruption | Planned Interruption Equipment
415 |  | 251010L5FSFMUZ | F419 to F450 |  | Fairlie F380 - Fairlie Rural | 2025-11-10 08:45 | 45971.3646 | 2025-11-10 17:10 | 45971.7153 | 0.6746 | 0.0014063 | 49 | 23505 | B | Planned interruption | Notified Interruption Equipment
416 |  | 251015WEHSBPTT | D11 |  | Temuka 01 - Temuka West | 2025-11-11 09:30 | 45972.3958 | 2025-11-11 13:52 | 45972.5778 | 0.0075194 | 2.87e-05 | 1 | 262 | B | Planned interruption | Planned Interruption Equipment
417 |  | 251010NXUFX7ZK | F419 to F450 |  | Fairlie F380 - Fairlie Rural | 2025-11-11 08:30 | 45972.3542 | 2025-11-11 15:20 | 45972.6389 | 0.53813 | 0.0014063 | 49 | 18750 | B | Planned interruption | Notified Interruption Equipment
418 |  | 251113GZLGLDS7 | Fuses TOB891 |  | Albury ABY2742 - Cave | 2025-11-12 13:33 | 45973.5646 | 2025-11-12 14:15 | 45973.5938 | 0.0012054 | 2.87e-05 | 1 | 42 | C | DefectiveEquipment | Repair Crossarm
419 |  | 251028Y7Y18T3N | TX B1505-02 |  | Timaru 2712 - Mountain View Road | 2025-11-13 08:00 | 45974.3333 | 2025-11-13 15:20 | 45974.6389 | 0.33617 | 0.001148 | 40 | 11713 | B | Planned interruption | Planned Interruption Equipment
420 |  | 251113FNU35FN1 | TX Fuses TOA1589 to end |  | Studholme 09 - Morven | 2025-11-12 19:37 | 45973.8174 | 2025-11-13 10:07 | 45974.4215 | 0.024969 | 2.87e-05 | 1 | 870 | C | ThirdPartyInterference | Safety Isolation
421 |  | 251117ON4WR6PM | ABS L340 to end minus pole #35627 to end |  | WSS CB11 Waipopo | 2025-11-15 17:57 | 45976.7479 | 2025-11-15 21:04 | 45976.8778 | 0.27434 | 0.0017507 | 61 | 9559 | C | DefectiveEquipment | Splice Failure
422 |  | 251020MS9V0KIM | B1959-06 |  | Timaru 2742 - Levels Plain | 2025-11-16 09:00 | 45977.375 | 2025-11-16 11:38 | 45977.4847 | 0.0045346 | 2.87e-05 | 1 | 158 | B | Planned interruption | Planned Interruption Equipment
423 |  | 251023ISNZ3EL8 | T118 |  | Temuka 02 - Milford | 2025-11-18 09:00 | 45979.375 | 2025-11-18 10:29 | 45979.4368 | 0.18647 | 0.0020951 | 73 | 6497 | B | Planned interruption | Planned Interruption Vegetation
424 |  | 251028TVB3CPEI | T680 |  | Temuka 09 - Waitohi | 2025-11-18 12:30 | 45979.5208 | 2025-11-18 14:56 | 45979.6222 | 0.058663 | 0.0004018 | 14 | 2044 | B | Planned interruption | Planned Interruption Equipment
425 |  | 251119GDXUAXRO | Fuses T420 |  | Geraldine G156 - Woodbury | 2025-11-18 22:59 | 45979.9576 | 2025-11-19 00:50 | 45980.0347 | 0.0892 | 0.0008036 | 28 | 3108 | C | CauseUnknown | Unknown
426 |  | 2510293AZCPNX0 | W155 |  | Bells Pond CB13 - Waikakahi | 2025-11-19 09:00 | 45980.375 | 2025-11-19 10:41 | 45980.4451 | 0.020291 | 0.0002009 | 7 | 707 | B | Planned interruption | Planned Interruption Vegetation
427 |  | 251021IQNFQJSA | TE126-LB H68 |  | Grasmere Street 12 - Selwyn Street | 2025-11-20 09:01 | 45981.3757 | 2025-11-20 14:31 | 45981.6049 | 0.58721 | 0.0017794 | 62 | 20460 | B | Planned interruption | Notified Interruption Equipment
428 |  | 25120123IMAWIV | Transformer - A1083 |  | Studholme 09 - Morven | 2025-11-20 19:24 | 45981.8083 | 2025-11-20 19:45 | 45981.8229 | 0.000574 | 5.74e-05 | 2 | 20 | C | ThirdPartyInterference | Stolen Earths
429 |  | 251010SZRLSLZD | TOB1728 |  | Albury ABY2742 - Cave | 2025-11-21 09:37 | 45982.4007 | 2025-11-21 12:22 | 45982.5153 | 0.0094711 | 5.74e-05 | 2 | 330 | B | Planned interruption | Planned Interruption Equipment
430 |  | 251121JSIWFBH9 | HNT CB 5 (Le Cren St) |  | Hunt Street 05 - Le Cren Street | 2025-11-21 14:58 | 45982.6236 | 2025-11-21 15:18 | 45982.6375 | 0.33522 | 0.016761 | 584 | 11680 | C | ThirdPartyInterference | Car Vs Pole
431 |  | 251023R2YMSI8U | W506 |  | Bells Pond CB13 - Waikakahi | 2025-11-24 10:00 | 45985.4167 | 2025-11-24 13:28 | 45985.5611 | 0.029848 | 0.0001435 | 5 | 1040 | B | Planned interruption | Planned Interruption Equipment
432 |  | 251029FUFLERDO | F210 |  | Fairlie F380 - Fairlie Rural | 2025-11-24 10:03 | 45985.4187 | 2025-11-24 14:31 | 45985.6049 | 0.030767 | 0.0001148 | 4 | 1072 | B | Planned interruption | Planned Interruption Equipment
433 |  | 251124ZJRQYTCR | ABS W327 |  | Pareora CB4 - St Andrews | 2025-11-24 13:28 | 45985.5611 | 2025-11-24 15:36 | 45985.65 | 0.062452 | 0.0004879 | 17 | 2176 | C | DefectiveEquipment | Cross Arm Replacement
434 |  | 251103HQBMXDJC | NST CB17 - RMU X4 - LB97-3 |  | North Street 17 - Stafford Street | 2025-11-24 09:16 | 45985.3861 | 2025-11-24 15:56 | 45985.6639 | 0.01148 | 2.87e-05 | 1 | 400 | B | Planned interruption | Planned Interruption Equipment
435 |  | 251118QGIVTBET | F243 |  | Fairlie F374 - Cricklewood | 2025-11-25 03:05 | 45986.1285 | 2025-11-25 03:20 | 45986.1389 | 0.0094711 | 0.0006314 | 22 | 330 | B | Planned interruption | Planned Interruption Equipment
436 |  | 251107CREIJJ3A | Pole 15506 to end |  | Fairlie F380 - Fairlie Rural | 2025-11-25 08:30 | 45986.3542 | 2025-11-25 16:12 | 45986.675 | 0.03797 | 8.6101e-05 | 3 | 1323 | B | Planned interruption | Notified Interruption Equipment
437 |  | 251106TVC8CD0B | T523 |  | Temuka 08 - Temuka East | 2025-11-25 09:00 | 45986.375 | 2025-11-25 15:37 | 45986.6507 | 0.091152 | 0.0002296 | 8 | 3176 | B | Planned interruption | Planned Interruption Vegetation
438 |  | 251120VXKBFFGF | F243 |  | Fairlie F374 - Cricklewood | 2025-11-26 02:08 | 45987.0889 | 2025-11-26 02:27 | 45987.1021 | 0.011997 | 0.0006314 | 22 | 418 | B | Planned interruption | Planned Interruption Equipment
439 |  | 2511270CCTAMKP | ABS M73 to CB M24 & SEC M272 |  | Tekapo M346 - Unwin Hut 33kV | 2025-11-26 13:26 | 45987.5597 | 2025-11-26 15:35 | 45987.6493 | 0.081451 | 0.0006314 | 22 | 2838 | C | DefectiveEquipment | Burnt / Broken crossarm form insulator failure
440 |  | 2511270CCTAMKP | ABS M73 to CB M24 & SEC M272 |  | Unwin Hut M158 - Mt Cook Village Roadside | 2025-11-26 13:23 | 45987.5576 | 2025-11-26 15:37 | 45987.6507 | 0.073071 | 0.0005453 | 19 | 2546 | C | DefectiveEquipment | Burnt / Broken crossarm form insulator failure
441 |  | 2511270CCTAMKP | ABS M73 to CB M24 & SEC M272 |  | Unwin Hut M159 - Mt Cook Village Hillside | 2025-11-26 13:23 | 45987.5576 | 2025-11-26 15:37 | 45987.6507 | 0.26921 | 0.002009 | 70 | 9380 | C | DefectiveEquipment | Burnt / Broken crossarm form insulator failure
442 |  | 251107VO6B59P9 | Pole 15506 to end |  | Fairlie F380 - Fairlie Rural | 2025-11-26 08:30 | 45987.3542 | 2025-11-26 16:20 | 45987.6806 | 0.039319 | 8.6101e-05 | 3 | 1370 | B | Planned interruption | Notified Interruption Equipment
443 |  | 251201G1TGEHVC | ABS L653 to Links L1490 P#27599 |  | Timaru 2712 - Mountain View Road | 2025-11-27 09:16 | 45988.3861 | 2025-11-27 15:06 | 45988.6292 | 1.6097 | 0.021525 | 750 | 56087 | C | ThirdPartyInterference | Bus V Pole
444 |  | 251028GQXRWQDB | LB6 towards DB2783 |  | Timaru 2702 - Morgans Road | 2025-11-27 08:30 | 45988.3542 | 2025-11-27 15:08 | 45988.6306 | 0.27053 | 0.0007462 | 26 | 9426 | B | Planned interruption | Planned Interruption Equipment
445 |  | 251128QAQVWSPL | L1348 - L196 |  | Pareora CB7 - Holmestation | 2025-11-27 15:28 | 45988.6444 | 2025-11-27 19:52 | 45988.8278 | 0.38616 | 0.0059983 | 209 | 13455 | C | DefectiveEquipment | Repair conductors at Pole #20401
446 |  | 251128YXYAD2RG | Fuses L110 - TX B561 |  | Pareora CB7 - Holmestation | 2025-11-27 16:01 | 45988.6674 | 2025-11-27 18:28 | 45988.7694 | 0.07353 | 0.0053382 | 186 | 2562 | C | DefectiveEquipment | Broken conductors at Tx B561
447 |  | 251128ABNB3OQK | TX A1530 |  | Studholme 02 - Glenavy | 2025-11-27 15:36 | 45988.65 | 2025-11-27 16:09 | 45988.6729 | 0.00094711 | 2.87e-05 | 1 | 33 | C | ThirdPartyInterference | Stolen Earths
448 |  | 251201ZNR07NPG | Transformer - A604 |  | Studholme 02 - Glenavy | 2025-11-27 14:15 | 45988.5938 | 2025-11-27 16:54 | 45988.7042 | 0.0045633 | 2.87e-05 | 1 | 159 | C | ThirdPartyInterference | Stolen Earths
449 |  | 25112832X4QDCE | L153 - END |  | Pareora CB6 - Normanby | 2025-11-27 15:54 | 45988.6625 | 2025-11-27 19:33 | 45988.8146 | 0.58712 | 0.0035588 | 124 | 20457 | C | VegetationInZone | Trees on Lines
450 |  | 251128STDR1CIO | Fuses T105 |  | Temuka 02 - Milford | 2025-11-27 17:02 | 45988.7097 | 2025-11-27 18:46 | 45988.7819 | 0.035818 | 0.0003444 | 12 | 1248 | C | DefectiveEquipment | Broken Jumper at fuses T105
451 |  | 251128XMW3RACT | CB F138 to Links F141 |  | Albury ABY2742 - Cave | 2025-11-27 15:54 | 45988.6625 | 2025-11-27 20:48 | 45988.8667 | 1.007 | 0.0065149 | 227 | 35088 | C | CauseUnknown | CB F138 trip on A&C phase OC reason Unknown
452 |  | 251128AFKKUL3Q | L821 to end |  | Timaru 2852 - Hadlow | 2025-11-27 16:16 | 45988.6778 | 2025-11-27 20:23 | 45988.8493 | 0.092156 | 0.0003731 | 13 | 3211 | C | VegetationInZone | Blown fuses L821 - trees
453 |  | 251128ROAIAQDB | L118 - End |  | Pareora CB4 - St Andrews | 2025-11-28 07:01 | 45989.2924 | 2025-11-28 08:43 | 45989.3632 | 0.014637 | 0.0001435 | 5 | 510 | C | CauseUnknown | No Power Call
454 |  | 251128ANBSUJY0 | TO B107 |  | Pareora CB7 - Holmestation | 2025-11-28 08:22 | 45989.3486 | 2025-11-28 09:31 | 45989.3965 | 0.037626 | 0.0005453 | 19 | 1311 | C | VegetationInZone | Branch on Lines
455 |  | 251128UTLTSKJP | TOB142 |  | Timaru 2852 - Hadlow | 2025-11-28 07:29 | 45989.3118 | 2025-11-28 10:10 | 45989.4236 | 0.0092415 | 5.74e-05 | 2 | 322 | C | VegetationInZone | Tree Branch on Lines
456 |  | 251201G07WNSKD | TOD1556 |  | Temuka 02 - Milford | 2025-11-28 11:00 | 45989.4583 | 2025-11-28 11:25 | 45989.4757 | 0.0007175 | 2.87e-05 | 1 | 25 | C | CauseUnknown | Carry out line patrol
457 |  | 251209F1T1JEIW | Transformer - A835 |  | Studholme 09 - Morven | 2025-11-28 13:57 | 45989.5813 | 2025-11-28 14:51 | 45989.6188 | 0.0030996 | 5.74e-05 | 2 | 108 | C | ThirdPartyInterference | Stolen Tx earthing A835
458 |  | 251201W8LSEEAF | TxA531 |  | Studholme 09 - Morven | 2025-11-28 13:55 | 45989.5799 | 2025-11-28 15:30 | 45989.6458 | 0.0027265 | 2.87e-05 | 1 | 95 | C | ThirdPartyInterference | Repair Earths
459 |  | 251128V8SBLNQD | Fuses L110 - TX B561 |  | Pareora CB7 - Holmestation | 2025-11-27 16:01 | 45988.6674 | 2025-11-28 16:30 | 45989.6875 | 0.061533 | 0.000287 | 10 | 2144 | C | DefectiveEquipment | Broken Pole t Tx B561
460 |  | 251110V2OBS3RK | G329 |  | Geraldine G191 - Geraldine Township | 2025-11-28 08:30 | 45989.3542 | 2025-11-28 18:22 | 45989.7653 | 1.7942 | 0.0031283 | 109 | 62514 | B | Planned interruption | Notified Interruption Equipment
461 |  | 251030PYA5ZZGO | ABS L1109 |  | Timaru 2742 - Levels Plain | 2025-11-30 09:00 | 45991.375 | 2025-11-30 11:42 | 45991.4875 | 0.0092989 | 5.74e-05 | 2 | 324 | B | Planned interruption | Planned Interruption Equipment
462 |  | 251120TVRAUFCP | F243 |  | Fairlie F374 - Cricklewood | 2025-12-01 05:29 | 45992.2285 | 2025-12-01 05:51 | 45992.2438 | 0.013891 | 0.0006314 | 22 | 484 | B | Planned interruption | Planned Interruption Equipment
463 |  | 251028MC9WGISH | Fuses F277 to ABS F314 |  | Fairlie F380 - Fairlie Rural | 2025-12-01 10:27 | 45992.4354 | 2025-12-01 12:29 | 45992.5201 | 0.09804 | 0.0008036 | 28 | 3416 | B | Planned interruption | Planned Interruption Equipment
464 |  | 251112E7ZZTAOD | F156 |  | Albury ABY2742 - Cave | 2025-12-01 15:00 | 45992.625 | 2025-12-01 15:14 | 45992.6347 | 0.1022 | 0.0075194 | 262 | 3561 | B | Planned interruption | Planned Interruption Equipment
465 |  | 2510285YKLN6PE | Pole 12396 to Pole 14943 |  | Albury ABY2742 - Cave | 2025-12-02 08:30 | 45993.3542 | 2025-12-02 10:09 | 45993.4229 | 0.008524 | 8.6101e-05 | 3 | 297 | B | Planned interruption | Planned Interruption Equipment
466 |  | 251203VZSHVGHO | L636 - End |  | Pareora CB7 - Holmestation | 2025-12-02 15:28 | 45993.6444 | 2025-12-02 16:43 | 45993.6965 | 0.47944 | 0.0089545 | 312 | 16705 | C | DefectiveEquipment | Defective Equipment
467 |  | 2511068OTIKGY4 | W486 - W710 - W267 + A942-03 |  | Studholme 03 - Waimate | 2025-12-02 08:00 | 45993.3333 | 2025-12-02 17:43 | 45993.7382 | 1.2963 | 0.0023247 | 81 | 45166 | B | Planned interruption | Notified Interruption Equipment
468 |  | 2511107RHPPKFD | B381-04+B1236-04 |  | Timaru 2832 - Grants Road | 2025-12-02 09:00 | 45993.375 | 2025-12-02 17:30 | 45993.7292 | 0.43911 | 0.00086101 | 30 | 15300 | B | Planned interruption | Planned Interruption Equipment
469 |  | 2512036I6S9DS3 | TOA1072 |  | Studholme 02 - Glenavy | 2025-12-03 11:02 | 45994.4597 | 2025-12-03 11:28 | 45994.4778 | 0.0007462 | 2.87e-05 | 1 | 26 | C | ThirdPartyInterference | Equipment Damage / Vandalism
470 |  | 251118SNCDS7WL | T641 |  | Temuka 08 - Temuka East | 2025-12-03 09:13 | 45994.384 | 2025-12-03 15:15 | 45994.6354 | 0.083116 | 0.0002296 | 8 | 2896 | B | Planned interruption | Planned Interruption Equipment
471 |  | 251204FNGP2BDQ | A1513-02 |  | Studholme 07 - Waihaorunga | 2025-12-03 12:19 | 45994.5132 | 2025-12-03 15:34 | 45994.6486 | 0.1264 | 0.0006601 | 23 | 4404 | C | DefectiveEquipment | Replace leaking Tx A1513
472 |  | 251006SAPIVXTI | T326 |  | Geraldine G194 - Speechley | 2025-12-03 09:00 | 45994.375 | 2025-12-03 15:43 | 45994.6549 | 0.15036 | 0.0003731 | 13 | 5239 | B | Planned interruption | Planned Interruption Vegetation
473 |  | 251209UKOMJA42 | A28 |  | Studholme 02 - Glenavy | 2025-12-03 17:24 | 45994.725 | 2025-12-03 17:59 | 45994.7493 | 0.002009 | 5.74e-05 | 2 | 70 | C | ThirdPartyInterference | Stolen earth wire at Tx A28
474 |  | 251209TPDR07L3 | A832 |  | Studholme 02 - Glenavy | 2025-12-03 18:07 | 45994.7549 | 2025-12-03 18:30 | 45994.7708 | 0.0006601 | 2.87e-05 | 1 | 23 | C | ThirdPartyInterference | Stolen eartha TX A832
475 |  | 251209MJJZQ8SG | B1785 |  | Pleasant Point CB2 - Sutherlands | 2025-12-03 20:23 | 45994.8493 | 2025-12-03 21:53 | 45994.9118 | 0.0064575 | 8.6101e-05 | 3 | 225 | C | DefectiveEquipment | Burnt LV tail Tx B1785
476 |  | 2512090ILYHWT5 | TO D842 |  | Temuka 07 - Rangitata | 2025-12-04 05:22 | 45995.2236 | 2025-12-04 06:49 | 45995.284 | 0.0024969 | 2.87e-05 | 1 | 87 | C | CauseUnknown | TX fuses Blown
477 |  | 2511126U8RM5A5 | M320 |  | Old Man Range M338 - Simons Pass | 2025-12-04 09:00 | 45995.375 | 2025-12-04 12:34 | 45995.5236 | 0.0061418 | 2.87e-05 | 1 | 214 | B | Planned interruption | Planned Interruption Equipment
478 |  | 251119WKTX2TI8 | TOC100 |  | Fairlie F380 - Fairlie Rural | 2025-12-04 09:23 | 45995.391 | 2025-12-04 12:53 | 45995.5368 | 0.017966 | 8.6101e-05 | 3 | 626 | B | Planned interruption | Planned Interruption Equipment
479 |  | 251126FSDKHAH3 | F243 |  | Fairlie F374 - Cricklewood | 2025-12-04 09:00 | 45995.375 | 2025-12-04 14:33 | 45995.6062 | 0.21026 | 0.0006314 | 22 | 7326 | B | Planned interruption | Planned Interruption Equipment
480 |  | 251111ZLYR4EPJ | ABS F230 |  | Fairlie F380 - Fairlie Rural | 2025-12-05 09:32 | 45996.3972 | 2025-12-05 14:20 | 45996.5972 | 0.14052 | 0.0004879 | 17 | 4896 | B | Planned interruption | Planned Interruption Equipment
481 |  | 251110JXOSCDF7 | W161 |  | Studholme 09 - Morven | 2025-12-05 09:00 | 45996.375 | 2025-12-05 14:21 | 45996.5979 | 0.064489 | 0.0002009 | 7 | 2247 | B | Planned interruption | Planned Interruption Vegetation
482 |  | 251205AVQLLCXT | CB W664 to RMU W699 |  | Studholme 07 - Waihaorunga | 2025-12-05 14:20 | 45996.5972 | 2025-12-05 14:54 | 45996.6208 | 0.46379 | 0.022989 | 801 | 16160 | C | AdverseWeather | Vegetation - High Winds
483 |  | 251205GM37PALS | Fuses W334 to end |  | Pareora CB7 - Holmestation | 2025-12-05 14:08 | 45996.5889 | 2025-12-05 16:21 | 45996.6813 | 0.0076342 | 5.74e-05 | 2 | 266 | C | AdverseWeather | Tree branch on lines
484 |  | 251209HRZFNRLM | W510 |  | Bells Pond CB12 - Ikawai | 2025-12-05 19:13 | 45996.8007 | 2025-12-05 20:28 | 45996.8528 | 0.019373 | 0.0002583 | 9 | 675 | C | Vegetation | W510 Blown fuses
485 |  | 251209MJSBNIBV | F227 |  | Fairlie F380 - Fairlie Rural | 2025-12-05 21:19 | 45996.8882 | 2025-12-05 23:50 | 45996.9931 | 0.052005 | 0.0003444 | 12 | 1812 | C | VegetationInZone | Tree & broken cross arm poles 15364-15399 & 15364
486 |  | 25111301Q3TK3B | L379+L380 |  | WSS CB14 Woolworks | 2025-12-06 09:00 | 45997.375 | 2025-12-06 15:24 | 45997.6417 | 0.064403 | 0.0001722 | 6 | 2244 | B | Planned interruption | Planned Interruption Equipment
487 |  | 251113NSAENTRC | TE71+TE21+TE1 |  | North Street 08 - Barnard Street | 2025-12-07 08:00 | 45998.3333 | 2025-12-07 10:01 | 45998.4174 | 0.31989 | 0.0029274 | 102 | 11146 | B | Planned interruption | Planned Interruption Equipment
488 |  | 251113880YGG65 | TOC497 |  | Albury ABY2732 - Raincliff | 2025-12-08 09:52 | 45999.4111 | 2025-12-08 13:23 | 45999.5576 | 0.0060557 | 2.87e-05 | 1 | 211 | B | Planned interruption | Planned Interruption Equipment
489 |  | 251114RF3QSGIF | TE61-14 |  | Grasmere Street 07 - Douglas Street | 2025-12-08 08:33 | 45999.3562 | 2025-12-08 15:24 | 45999.6417 | 0.18873 | 0.0004592 | 16 | 6576 | B | Planned interruption | Planned Interruption Equipment
490 |  | 251113TQKEFOZ7 | B197-01 |  | Timaru 2832 - Grants Road | 2025-12-08 09:00 | 45999.375 | 2025-12-08 16:19 | 45999.6799 | 0.37798 | 0.00086101 | 30 | 13170 | B | Planned interruption | Planned Interruption Equipment
491 |  | 25120972NPITQK | LBS L1339 |  | WSS CB11 Waipopo | 2025-12-08 18:15 | 45999.7604 | 2025-12-08 19:21 | 45999.8063 | 0.28413 | 0.004305 | 150 | 9900 | C | DefectiveEquipment | Repair broken jumper @ Tx B2030
492 |  | 2511195NQDJLJD | TOA531 |  | Studholme 09 - Morven | 2025-12-09 10:00 | 46000.4167 | 2025-12-09 12:06 | 46000.5042 | 0.0036162 | 2.87e-05 | 1 | 126 | B | Planned interruption | Planned Interruption Equipment
493 |  | 251120DLQNIXHS | Pole #08357 |  | Geraldine G156 - Woodbury | 2025-12-09 08:30 | 46000.3542 | 2025-12-09 12:24 | 46000.5167 | 0.013001 | 5.74e-05 | 2 | 453 | B | Planned interruption | Planned Interruption Equipment
494 |  | 251119EHGXM8XA | G129 |  | Geraldine G194 - Speechley | 2025-12-09 08:05 | 46000.3368 | 2025-12-09 14:46 | 46000.6153 | 0.14376 | 0.0003731 | 13 | 5009 | B | Planned interruption | Notified Interruption Equipment
495 |  | 251212R4SCO9K7 | TX B494 |  | Timaru 2712 - Mountain View Road | 2025-12-09 13:53 | 46000.5785 | 2025-12-09 15:38 | 46000.6514 | 0.0090406 | 8.6101e-05 | 3 | 315 | C | HumanError | Remove TX B494 from damaged structure
496 |  | 251121JNMRTFOG | TOA636 |  | Bells Pond CB13 - Waikakahi | 2025-12-10 09:40 | 46001.4028 | 2025-12-10 13:52 | 46001.5778 | 0.0072324 | 2.87e-05 | 1 | 252 | B | Planned interruption | Planned Interruption Equipment
497 |  | 251209USPMKT6J | Z452 |  | Twizel TVS03 - Pukaki | 2025-12-10 11:14 | 46001.4681 | 2025-12-10 13:59 | 46001.5826 | 0.08524 | 0.0005166 | 18 | 2970 | B | Planned interruption | Planned Interruption Equipment
498 |  | 251119E1H1CFT7 | W693 |  | Studholme 09 - Morven | 2025-12-11 09:50 | 46002.4097 | 2025-12-11 10:23 | 46002.4326 | 0.00094711 | 2.87e-05 | 1 | 33 | B | Planned interruption | Planned Interruption Equipment
499 |  | 2511197BLBIKXB | G138 Pole #08424 |  | Geraldine G194 - Speechley | 2025-12-11 08:00 | 46002.3333 | 2025-12-11 14:30 | 46002.6042 | 0.7037 | 0.0018368 | 64 | 24519 | B | Planned interruption | Notified Interruption Equipment
500 |  | 251110CYQMWKSQ | Z440 - Tx E108-03 |  | TVS11 - Urban No2 | 2025-12-11 09:00 | 46002.375 | 2025-12-11 15:37 | 46002.6507 | 1.1778 | 0.0031283 | 109 | 41039 | B | Planned interruption | Notified Interruption Equipment
501 |  | 2512112PB1NJ3I | L1496 to L225 |  | Pleasant Point CB4 - Totara Valley | 2025-12-11 16:06 | 46002.6708 | 2025-12-11 18:46 | 46002.7819 | 0.36237 | 0.0036736 | 128 | 12626 | C | CauseUnknown | Several Earth Fault Trip & Auto Reclose on CB L107
502 |  | 251218WRPJNESO | TOA239 |  | Studholme 02 - Glenavy | 2025-12-11 18:30 | 46002.7708 | 2025-12-12 08:28 | 46003.3528 | 0.024051 | 2.87e-05 | 1 | 838 | C | Lightning | Lightning - Blown Fuse
503 |  | 251213IMHKIIWE | #61 Willowbridge Settlement Rd |  | Studholme 09 - Morven | 2025-12-12 05:20 | 46003.2222 | 2025-12-12 17:56 | 46003.7472 | 0.17719 | 0.0004592 | 16 | 6174 | C | DefectiveEquipment | Lightning damaged Tx A1013
504 |  | 2512180TBKMQFW | TOA725 |  | Bells Pond CB13 - Waikakahi | 2025-12-11 18:30 | 46002.7708 | 2025-12-12 09:22 | 46003.3903 | 0.12743 | 0.0001435 | 5 | 4440 | C | Lightning | Lightning
505 |  | 251213JXB1FMHE | TO A197 |  | Studholme 02 - Glenavy | 2025-12-12 05:43 | 46003.2382 | 2025-12-13 12:25 | 46004.5174 | 0.071808 | 0.0001722 | 6 | 2502 | C | DefectiveEquipment | Faulty Tx A197
506 |  | 2512189FEZXOU5 | TOA988 |  | Studholme 09 - Morven | 2025-12-11 19:16 | 46002.8028 | 2025-12-12 11:37 | 46003.484 | 0.056224 | 5.74e-05 | 2 | 1959 | C | Lightning | Lightning
507 |  | 251121WQDVID5E | W537 |  | Bells Pond CB1 - Waihuna | 2025-12-12 11:00 | 46003.4583 | 2025-12-12 11:55 | 46003.4965 | 0.0078925 | 0.0001435 | 5 | 275 | B | Planned interruption | Planned Interruption Equipment
508 |  | 251119SB9WTXGU | F158 |  | Albury ABY2742 - Cave | 2025-12-12 09:33 | 46003.3979 | 2025-12-12 12:14 | 46003.5097 | 0.018483 | 0.0001148 | 4 | 644 | B | Planned interruption | Planned Interruption Equipment
509 |  | 251119ZYGTGFMU | F252 |  | Fairlie F380 - Fairlie Rural | 2025-12-12 09:24 | 46003.3917 | 2025-12-12 12:54 | 46003.5375 | 0.030135 | 0.0001435 | 5 | 1050 | B | Planned interruption | Planned Interruption Equipment
510 |  | 251119NET1MM8Q | F258 |  | Fairlie F380 - Fairlie Rural | 2025-12-12 10:07 | 46003.4215 | 2025-12-12 14:51 | 46003.6188 | 0.024453 | 8.6101e-05 | 3 | 852 | B | Planned interruption | Planned Interruption Equipment
511 |  | 2512131VXSYMPW | TOD1422 |  | Rangitata 03 - Mahan Road | 2025-12-13 12:18 | 46004.5125 | 2025-12-13 13:01 | 46004.5424 | 0.0012341 | 2.87e-05 | 1 | 43 | C | CauseUnknown | Unknown - Blown Tx Fuses
512 |  | 251125CWSAEARP | TEX60 |  | North Street 10 - Fraser Street | 2025-12-14 08:00 | 46005.3333 | 2025-12-14 18:25 | 46005.7674 | 0.035674 | 5.74e-05 | 2 | 1243 | B | Planned interruption | Planned Interruption Equipment
513 |  | 251208DDFDN3EM | F463 to poles #14943/14944 |  | Albury ABY2742 - Cave | 2025-12-15 08:33 | 46006.3562 | 2025-12-15 14:36 | 46006.6083 | 0.031254 | 8.6101e-05 | 3 | 1089 | B | Planned interruption | Planned Interruption Equipment
514 |  | 251218M5B6QXWE | HVFeeder - Pareora - Works No 1 and 2 |  | Pareora - Works No 1 and 2 | 2025-12-15 13:32 | 46006.5639 | 2025-12-15 14:46 | 46006.6153 | 0.0021238 | 2.87e-05 | 1 | 74 | C | HumanError | PAR Sub trip
515 |  | 251218M5B6QXWE | HVFeeder - Pareora - Works No 1 and 2 |  | Pareora CB4 - St Andrews | 2025-12-15 13:32 | 46006.5639 | 2025-12-15 14:49 | 46006.6174 | 0.90827 | 0.011796 | 411 | 31647 | C | HumanError | PAR Sub trip
516 |  | 251218M5B6QXWE | HVFeeder - Pareora - Works No 1 and 2 |  | Pareora CB6 - Normanby | 2025-12-15 13:32 | 46006.5639 | 2025-12-15 14:51 | 46006.6188 | 1.2992 | 0.016445 | 573 | 45267 | C | HumanError | PAR Sub trip
517 |  | 251218M5B6QXWE | HVFeeder - Pareora - Works No 1 and 2 |  | Pareora CB7 - Holmestation | 2025-12-15 13:32 | 46006.5639 | 2025-12-15 14:53 | 46006.6201 | 0.70904 | 0.0087536 | 305 | 24705 | C | HumanError | PAR Sub trip
518 |  | 251125EWTKR0VY | TOB345 |  | Albury ABY2742 - Cave | 2025-12-15 09:00 | 46006.375 | 2025-12-15 16:01 | 46006.6674 | 0.012083 | 2.87e-05 | 1 | 421 | B | Planned interruption | Planned Interruption Equipment
519 |  | 251127DZMIPHTK | F442 |  | Albury ABY2742 - Cave | 2025-12-16 09:00 | 46007.375 | 2025-12-16 10:35 | 46007.441 | 0.035445 | 0.0003731 | 13 | 1235 | B | Planned interruption | Planned Interruption Vegetation
520 |  | 251121DZKL5AOO | TOA162 |  | Studholme 08 - Mount Studholme | 2025-12-16 09:00 | 46007.375 | 2025-12-16 10:39 | 46007.4437 | 0.0028413 | 2.87e-05 | 1 | 99 | B | Planned interruption | Planned Interruption Vegetation
521 |  | 251124IGZSDFDM | TOB756 |  | Pleasant Point CB5 - Pleasant Point Township | 2025-12-16 09:00 | 46007.375 | 2025-12-16 13:36 | 46007.5667 | 0.0079212 | 2.87e-05 | 1 | 276 | B | Planned interruption | Planned Interruption Equipment
522 |  | 251219IBBHHFK1 | CB2972 - Tx B225 |  | Timaru 2972 - Smithfield | 2025-12-16 12:07 | 46007.5049 | 2025-12-18 10:00 | 46009.4167 | 0.56967 | 0.0035875 | 125 | 19849 | C | DefectiveEquipment | Broken P#24456
523 |  | 251119D7UFSIM7 | G138 - Pole #08199 |  | Geraldine G194 - Speechley | 2025-12-16 08:28 | 46007.3528 | 2025-12-16 14:35 | 46007.6076 | 0.1621 | 0.0004592 | 16 | 5648 | B | Planned interruption | Notified Interruption Equipment
524 |  | 251125SWSYDEVP | E258-03 |  | TVS11 - Urban No2 | 2025-12-16 10:14 | 46007.4264 | 2025-12-16 14:36 | 46007.6083 | 0.051775 | 0.0002009 | 7 | 1804 | B | Planned interruption | Planned Interruption Equipment
525 |  | 2512124CBDJLDQ | TX B494 '01' LV Main isolator to end - pole #28411 to end |  | Timaru 2712 - Mountain View Road | 2025-12-16 08:57 | 46007.3729 | 2025-12-16 15:59 | 46007.666 | 0.33726 | 0.0008036 | 28 | 11751 | B | Planned interruption | Planned Interruption Equipment
526 |  | 251217MRJU0T5S | 1pH ICP Tx D1735 |  | Rangitata 12 - Orton | 2025-12-16 10:20 | 46007.4306 | 2025-12-17 11:05 | 46008.4618 | 0.13013 | 0.0004879 | 17 | 4534 | C | DefectiveEquipment | Replace Tx D1735
527 |  | 260105DOXSPBE5 | Fuses F123 to end minus TX B394 |  | Pleasant Point CB4 - Totara Valley | 2025-12-16 15:57 | 46007.6646 | 2025-12-17 11:30 | 46008.4792 | 0.11509 | 0.000287 | 10 | 4010 | C | Lightning | Lightning Strike
528 |  | 251121WURZLSD4 | TOD67 |  | Temuka 03 - Winchester | 2025-12-17 09:00 | 46008.375 | 2025-12-17 14:10 | 46008.5903 | 0.026289 | 8.6101e-05 | 3 | 916 | B | Planned interruption | Planned Interruption Equipment
529 |  | 251217GDPFESPR | TO B890 |  | Albury ABY2742 - Cave | 2025-12-16 21:42 | 46007.9042 | 2025-12-17 15:00 | 46008.625 | 0.029791 | 2.87e-05 | 1 | 1038 | C | DefectiveEquipment | Faulty Tx
530 |  | 251127XAAOHCBS | G325+TX37 |  | Geraldine G194 - Speechley | 2025-12-17 08:14 | 46008.3431 | 2025-12-17 15:02 | 46008.6264 | 0.46839 | 0.001148 | 40 | 16320 | B | Planned interruption | Planned Interruption Vegetation
531 |  | 251217QNEFYQ7J | TO B1406 |  | Timaru 2942 - Old North Road | 2025-12-17 13:21 | 46008.5563 | 2025-12-17 15:24 | 46008.6417 | 0.017651 | 0.0001435 | 5 | 615 | C | DefectiveEquipment | Faulty 11kV cable
532 |  | 251219GVN6QOUA | TE50 |  | Grasmere Street 05 - Nile Street | 2025-12-18 10:15 | 46009.4271 | 2025-12-19 08:57 | 46010.3729 | 0.31714 | 0.0097581 | 340 | 11050 | C | DefectiveEquipment | Water ingress on HV equipment GRM Sub
533 |  | 2511276FVBYGNA | G181 |  | Geraldine G156 - Woodbury | 2025-12-18 08:33 | 46009.3562 | 2025-12-18 11:33 | 46009.4812 | 0.092989 | 0.0005166 | 18 | 3240 | B | Planned interruption | Planned Interruption Vegetation
534 |  | 251218NTQSJ3EC | Z481-Z499 |  | Twizel TVS02 - Glen Lyon | 2025-12-18 11:45 | 46009.4896 | 2025-12-18 12:45 | 46009.5312 | 0.15713 | 0.0026978 | 94 | 5475 | C | DefectiveEquipment | Lower X arm on Red tagged pole
535 |  | 251216CAI2MKXK | TX36 towards TX37 |  | Temuka 09 - Waitohi | 2025-12-18 09:20 | 46009.3889 | 2025-12-18 12:52 | 46009.5361 | 0.22512 | 0.0010619 | 37 | 7844 | B | Planned interruption | Planned Interruption Equipment
536 |  | 251212SPARADMO | TX B494 '01' LV Main isolator to end - pole #28411 to end |  | Timaru 2712 - Mountain View Road | 2025-12-18 08:30 | 46009.3542 | 2025-12-18 13:49 | 46009.5757 | 0.24665 | 0.0008036 | 28 | 8594 | B | Planned interruption | Planned Interruption Equipment
537 |  | 251219ZHM9CXGM | P#17713 ICPs |  | Albury ABY2742 - Cave | 2025-12-16 13:00 | 46007.5417 | 2025-12-18 14:55 | 46009.6215 | 0.42646 | 0.0001435 | 5 | 14859 | C | DefectiveEquipment | Faulty Tx C20
538 |  | 251218LTLWP1FR | F176 |  | Albury ABY2742 - Cave | 2025-12-16 19:30 | 46007.8125 | 2025-12-18 14:40 | 46009.6111 | 0.078179 | 5.74e-05 | 2 | 2724 | C | Lightning | Replace TX C255
539 |  | 251205U8CXYYIN | ABS F156 |  | Albury ABY2742 - Cave | 2025-12-18 15:50 | 46009.6597 | 2025-12-18 15:56 | 46009.6639 | 0.045117 | 0.0075194 | 262 | 1572 | B | Planned interruption | Planned Interruption Equipment
540 |  | 251219R4O0YXIP | DB2975 |  | Timaru 2942 - Old North Road | 2025-12-18 16:42 | 46009.6958 | 2025-12-18 17:07 | 46009.7132 | 0.0035301 | 0.0001435 | 5 | 123 | C | DefectiveEquipment | Replace faulty cable Tx B1406
541 |  | 251219COYGVRSP | M201 |  | Old Man Range M338 - Simons Pass | 2025-12-18 22:13 | 46009.9257 | 2025-12-19 10:22 | 46010.4319 | 1.0252 | 0.0014063 | 49 | 35721 | C | Wildlife | Repair Broken Lines P#55902
542 |  | 251220RH2A2NL3 | ABS F212 - ABS F348 |  | Albury ABY2732 - Raincliff | 2025-12-20 08:10 | 46011.3403 | 2025-12-20 09:23 | 46011.391 | 0.019401 | 0.000287 | 10 | 676 | C | DefectiveEquipment | TX C64 replacement
543 |  | 260109KZPBPL1P | ABS F212- ABS F348 |  | Albury ABY2732 - Raincliff | 2025-12-20 08:10 | 46011.3403 | 2025-12-20 09:23 | 46011.391 | 0.019401 | 0.000287 | 10 | 676 | C | DefectiveEquipment | Transformer Replacement
544 |  | 260112MHJP3NMF | Fuses TO D1784 |  | Rangitata 04 - Main South Road | 2025-12-20 17:15 | 46011.7188 | 2025-12-21 10:35 | 46012.441 | 0.38501 | 0.0026978 | 94 | 13415 | C | DefectiveEquipment | A & C PHASE FAULT
545 |  | 25122392YETV7C | Fuses TO B1159 to end |  | WSS CB7 Arowhenua and LS1 | 2025-12-22 09:10 | 46013.3819 | 2025-12-22 10:47 | 46013.4493 | 0.0027839 | 2.87e-05 | 1 | 97 | C | CauseUnknown | Unknown
546 |  | 251223QZZU396L | Fuses TO B63 |  | Pleasant Point CB2 - Sutherlands | 2025-12-23 10:16 | 46014.4278 | 2025-12-23 13:01 | 46014.5424 | 0.0047355 | 2.87e-05 | 1 | 165 | C | DefectiveEquipment | Red Tagged pole replacement
547 |  | 251223TQSXD6ZO | PAR CB4 to end |  | Pareora CB4 - St Andrews | 2025-12-23 17:12 | 46014.7167 | 2025-12-23 17:29 | 46014.7285 | 0.20638 | 0.01214 | 423 | 7191 | C | ThirdPartyInterference | Safety Isolation for truck vs lines
548 |  | 251224MPNTQ2B2 | ABS T630 to end |  | Rangitata 13 - Rangitata Island | 2025-12-24 09:08 | 46015.3806 | 2025-12-24 10:44 | 46015.4472 | 0.0053382 | 5.74e-05 | 2 | 186 | C | CauseUnknown | Unknown
549 |  | 25122436FVJQGP | Fuses L707 to Fuses L713 |  | Timaru 2852 - Hadlow | 2025-12-24 14:45 | 46015.6146 | 2025-12-24 16:07 | 46015.6715 | 0.044055 | 0.0006601 | 23 | 1535 | C | VegetationInZone | Tree branch on lines
550 |  | 251227FQMXYSSN | FLE CB F374 to end |  | Fairlie F383 - Fairlie Township | 2025-12-27 14:14 | 46018.5931 | 2025-12-27 14:22 | 46018.5986 | 0.081968 | 0.010246 | 357 | 2856 | C | Lightning | Lightning strike on transpower 110kV ABY line
551 |  | 251227FQMXYSSN | FLE CB F374 to end |  | Fairlie F380 - Fairlie Rural | 2025-12-27 14:14 | 46018.5931 | 2025-12-27 14:22 | 46018.5986 | 0.18024 | 0.02253 | 785 | 6280 | C | Lightning | Lightning strike on transpower 110kV ABY line
552 |  | 251227FQMXYSSN | FLE CB F374 to end |  | Fairlie F374 - Cricklewood | 2025-12-27 14:14 | 46018.5931 | 2025-12-27 14:23 | 46018.5993 | 0.013432 | 0.0014924 | 52 | 468 | C | Lightning | Lightning strike on transpower 110kV ABY line
553 |  | 260105TZBGKJON | Icp - 0007254806AL32C |  | Geraldine G156 - Woodbury | 2025-12-27 12:08 | 46018.5056 | 2025-12-28 15:58 | 46019.6653 | 0.6552 | 0.002296 | 80 | 22829 | C | Lightning | Lightning storm
554 |  | 251227W6MZYMFN | Fuses F208 to end |  | Fairlie F374 - Cricklewood | 2025-12-27 17:46 | 46018.7403 | 2025-12-27 20:50 | 46018.8681 | 0.031685 | 0.0001722 | 6 | 1104 | C | Lightning | Lightning
555 |  | 251228PPDNZQUY | ABS L1239 to end minus ABS L820 minus TX B1048 |  | Pleasant Point CB2 - Sutherlands | 2025-12-27 18:52 | 46018.7861 | 2025-12-28 12:01 | 46019.5007 | 0.096433 | 0.0004592 | 16 | 3360 | C | Lightning | Lightning Strike
556 |  | 2601066JNUDIJG | D1446 |  | Rangitata 04 - Main South Road | 2025-12-30 11:01 | 46021.459 | 2025-12-31 13:55 | 46022.5799 | 0.11885 | 0.000574 | 20 | 4141 | C | Lightning | Replace faulty Tx D1446
557 |  | 260101GDYEHWH1 | F173 to end |  | Albury ABY2742 - Cave | 2026-01-01 10:53 | 46023.4535 | 2026-01-01 12:48 | 46023.5333 | 0.046207 | 0.0004018 | 14 | 1610 | C | DefectiveEquipment | F173 fuses blown
558 |  | 260126FTZN1OP7 | L1415 to L509 |  | Timaru 2952 - Highfield | 2026-01-03 02:05 | 46025.0868 | 2026-01-03 06:58 | 46025.2903 | 5.231 | 0.033895 | 1181 | 182264 | C | CauseUnknown | TIM CB2952 and CB L509 trip
559 |  | 260109FFAW1PMV | W742 |  | Studholme 09 - Morven | 2026-01-03 11:00 | 46025.4583 | 2026-01-03 12:30 | 46025.5208 | 0.033579 | 0.0003731 | 13 | 1170 | C | ThirdPartyInterference | Repair damaged conductor caused by Grain Auger
560 |  | 260105RMR2VL1G | G201 Fuses |  | Geraldine G194 - Speechley | 2026-01-04 20:18 | 46026.8458 | 2026-01-05 11:36 | 46027.4833 | 0.046092 | 0.0002583 | 9 | 1606 | C | DefectiveEquipment | Replace Faulty Tx D125
561 |  | 260106KAJIQ1JB | W506 |  | Bells Pond CB13 - Waikakahi | 2026-01-06 09:53 | 46028.4118 | 2026-01-06 12:00 | 46028.5 | 0.36056 | 0.0049651 | 173 | 12563 | C | ThirdPartyInterference | CB W515 HI Aphase Grnd/Neutral Crurrent
562 |  | 260108KSUCPULV | Fuses F178 |  | Albury ABY2742 - Cave | 2026-01-08 12:26 | 46030.5181 | 2026-01-08 15:10 | 46030.6319 | 0.01412 | 8.6101e-05 | 3 | 492 | C | DefectiveEquipment | Blown Fuses
563 |  | 260109BJHDJPZI | HVFeeder - Geraldine G194 - Speechley |  | Geraldine G194 - Speechley | 2026-01-08 15:32 | 46030.6472 | 2026-01-08 18:20 | 46030.7639 | 0.5761 | 0.012398 | 432 | 20073 | C | ThirdPartyInterference | Car V Pole #874766
564 |  | 260111DV4VIPVE | CB W366 to Tripsavers W308 |  | Studholme 01 - Otaio | 2026-01-10 21:51 | 46032.9104 | 2026-01-11 03:22 | 46033.1403 | 0.7896 | 0.0097007 | 338 | 27512 | C | CauseUnknown | lines down cause Unknown
565 |  | 260111E3TKTIMJ | CB W664 to RMU W699 |  | Studholme 07 - Waihaorunga | 2026-01-11 13:41 | 46033.5701 | 2026-01-11 14:36 | 46033.6083 | 0.67414 | 0.022989 | 801 | 23489 | C | VegetationInZone | Tree on line
566 |  | 260111WRZEKDO6 | CB W411 |  | Studholme 02 - Glenavy | 2026-01-11 13:07 | 46033.5465 | 2026-01-11 14:11 | 46033.591 | 0.14511 | 0.0022673 | 79 | 5056 | C | VegetationOutZone | Tree branch on line
567 |  | 260203DSSBLO6P | Transformer - A1071 |  | Studholme 02 - Glenavy | 2026-01-11 12:28 | 46033.5194 | 2026-01-11 14:50 | 46033.6181 | 0.012226 | 8.6101e-05 | 3 | 426 | C | VegetationOutZone | Branch on line
568 |  | 260203R84UP5SE | Pole #33563 Temp Fuses |  | Studholme 08 - Mount Studholme | 2026-01-11 12:24 | 46033.5167 | 2026-01-11 15:10 | 46033.6319 | 0.066699 | 0.0004018 | 14 | 2324 | C | CauseUnknown | Unknown
569 |  | 260111IPSSFSIC | Transformer - A1269 |  | Studholme 08 - Mount Studholme | 2026-01-11 12:36 | 46033.525 | 2026-01-11 15:11 | 46033.6326 | 0.062279 | 0.0004018 | 14 | 2170 | C | DefectiveEquipment | unknown
570 |  | 260203ZPJHSKM4 | Transformer - C452 |  | Fairlie F380 - Fairlie Rural | 2026-01-11 14:40 | 46033.6111 | 2026-01-11 17:51 | 46033.7438 | 0.0054817 | 2.87e-05 | 1 | 191 | C | CauseUnknown | Unknown
571 |  | 251208ZKF4PXPZ | W499 - W220 |  | Studholme 08 - Mount Studholme | 2026-01-12 09:00 | 46034.375 | 2026-01-12 10:58 | 46034.4569 | 0.42571 | 0.0036449 | 127 | 14833 | B | Planned interruption | Planned Interruption Vegetation
572 |  | 2512104MNJAXH1 | TOD2047 |  | Temuka 02 - Milford | 2026-01-12 09:39 | 46034.4021 | 2026-01-12 13:30 | 46034.5625 | 0.0066297 | 2.87e-05 | 1 | 231 | B | Planned interruption | Planned Interruption Equipment
573 |  | 251208LD2SRPKR | W247 |  | Studholme 08 - Mount Studholme | 2026-01-12 13:30 | 46034.5625 | 2026-01-12 15:29 | 46034.6451 | 0.14344 | 0.0012054 | 42 | 4998 | B | Planned interruption | Planned Interruption Vegetation
574 |  | 251208NX9ZFXGW | L427-L487+L426 |  | Timaru 2942 - Old North Road | 2026-01-12 09:12 | 46034.3833 | 2026-01-12 16:24 | 46034.6833 | 0.037081 | 8.6101e-05 | 3 | 1292 | B | Planned interruption | Planned Interruption Equipment
575 |  | 260120NXH0VVSV | ABS W136 - ABS W158 - Fuses W105- CB W515 |  | Bells Pond CB13 - Waikakahi | 2026-01-12 21:02 | 46034.8764 | 2026-01-13 03:00 | 46035.125 | 0.81853 | 0.0078351 | 273 | 28520 | C | DefectiveEquipment | BPD CB13 Trip
576 |  | 251208Z0C9R7JT | TOA224 |  | Studholme 01 - Otaio | 2026-01-13 09:00 | 46035.375 | 2026-01-13 10:26 | 46035.4347 | 0.0049364 | 5.74e-05 | 2 | 172 | B | Planned interruption | Planned Interruption Vegetation
577 |  | 2601144DWFDQNK | G300 |  | Temuka 03 - Winchester | 2026-01-13 12:07 | 46035.5049 | 2026-01-13 13:10 | 46035.5486 | 0.11029 | 0.0017507 | 61 | 3843 | C | DefectiveEquipment | Repair Blown Load Side Jumper at Fuses G117
578 |  | 251208JJKI8CWJ | W232 |  | Studholme 08 - Mount Studholme | 2026-01-13 13:00 | 46035.5417 | 2026-01-13 14:08 | 46035.5889 | 0.023419 | 0.0003444 | 12 | 816 | B | Planned interruption | Planned Interruption Vegetation
579 |  | 2512086GSHZAY1 | G121 to links G128 |  | Geraldine G191 - Geraldine Township | 2026-01-13 09:28 | 46035.3944 | 2026-01-13 15:05 | 46035.6285 | 0.94636 | 0.00287 | 100 | 32974 | B | Planned interruption | Planned Interruption Equipment
580 |  | 260120YWQ7EWPW | Links G121 - RMU G327 |  | Geraldine G191 - Geraldine Township | 2026-01-13 18:54 | 46035.7875 | 2026-01-13 19:15 | 46035.8021 | 0.28046 | 0.017048 | 594 | 9772 | C | DefectiveEquipment | RMU G122 High PD
581 |  | 251208WNSBMVSY | F280-TOC388 |  | Fairlie F383 - Fairlie Township | 2026-01-15 09:16 | 46037.3861 | 2026-01-15 09:44 | 46037.4056 | 0.019287 | 0.0006888 | 24 | 672 | B | Planned interruption | Planned Interruption Equipment
582 |  | 251208JD8HAHFJ | L830 |  | Timaru 2852 - Hadlow | 2026-01-15 08:30 | 46037.3542 | 2026-01-15 12:20 | 46037.5139 | 0.16503 | 0.0007175 | 25 | 5750 | B | Planned interruption | Planned Interruption Equipment
583 |  | 260115XSWJY4HO | F225 |  | Fairlie F380 - Fairlie Rural | 2026-01-15 09:13 | 46037.384 | 2026-01-15 15:33 | 46037.6479 | 0.12763 | 0.001435 | 50 | 4447 | C | DefectiveEquipment | Replace TX C619
584 |  | 260120NLJXVX29 | ABS T116 - Fuses T119 |  | Temuka 02 - Milford | 2026-01-17 15:25 | 46039.6424 | 2026-01-17 18:46 | 46039.7819 | 0.58921 | 0.010332 | 360 | 20530 | C | Vegetation | Trees on Line
585 |  | 260119P16VPN9R | Transformer - B1979 |  | Pleasant Point CB4 - Totara Valley | 2026-01-19 09:30 | 46041.3958 | 2026-01-19 09:39 | 46041.4021 | 0.0002583 | 2.87e-05 | 1 | 9 | C | ThirdPartyInterference | Customer requested tap change for solar export
586 |  | 260119LNVVE6YO | HVFeeder - Geraldine G156 - Woodbury |  | Geraldine G156 - Woodbury | 2026-01-19 09:42 | 46041.4042 | 2026-01-19 11:19 | 46041.4715 | 2.0323 | 0.020951 | 730 | 70810 | C | Wildlife | Unknown
587 |  | 260119LNVVE6YO | HVFeeder - Geraldine G156 - Woodbury |  | Geraldine G191 - Geraldine Township | 2026-01-19 09:42 | 46041.4042 | 2026-01-19 11:19 | 46041.4715 | 4.2705 | 0.044026 | 1534 | 148798 | C | Wildlife | Unknown
588 |  | 260119LNVVE6YO | HVFeeder - Geraldine G156 - Woodbury |  | Geraldine G194 - Speechley | 2026-01-19 09:42 | 46041.4042 | 2026-01-19 11:20 | 46041.4722 | 1.2516 | 0.012772 | 445 | 43610 | C | Wildlife | Unknown
589 |  | 260119YT6XDPO4 | Fuses W257 |  | Studholme 07 - Waihaorunga | 2026-01-19 18:00 | 46041.75 | 2026-01-19 19:07 | 46041.7965 | 0.01346 | 0.0002009 | 7 | 469 | C | DefectiveEquipment | Re-hang Tx A922
590 |  | 2601125JAKHWT1 | NST04 - TEP26 - TE130 |  | North Street 04 - Rose Street | 2026-01-19 08:35 | 46041.3576 | 2026-01-20 02:35 | 46042.1076 | 0.80668 | 0.0022386 | 78 | 28107 | B | Planned interruption | Planned Interruption Equipment
591 |  | 2512159NRCTU7J | T111 |  | Temuka 02 - Milford | 2026-01-20 08:30 | 46042.3542 | 2026-01-20 16:50 | 46042.7014 | 0.2831 | 0.0006027 | 21 | 9864 | B | Planned interruption | Notified Interruption Equipment
592 |  | 2512153FHKP8KP | W133 |  | Bells Pond CB13 - Waikakahi | 2026-01-20 08:00 | 46042.3333 | 2026-01-20 18:30 | 46042.7708 | 0.18968 | 0.0003157 | 11 | 6609 | B | Planned interruption | Notified Interruption Equipment
593 |  | 260121ESSLLHUG | BPD CB1 [Waihun] |  | Bells Pond CB1 - Waihuna | 2026-01-21 09:50 | 46043.4097 | 2026-01-21 13:52 | 46043.5778 | 0.23184 | 0.0026117 | 91 | 8078 | C | ThirdPartyInterference | Repair Broken lines between P#31376 & P#31377
594 |  | 260220EZPBTB1V | CB G191 to RMU G275 |  | Geraldine G191 - Geraldine Township | 2026-01-21 11:47 | 46043.491 | 2026-01-21 13:59 | 46043.5826 | 8.9198 | 0.10476 | 3650 | 310793 | C | Wildlife | Magpie V Lines
595 |  | 260220EZPBTB1V | CB G191 to RMU G275 |  | Temuka 03 - Winchester | 2026-01-21 13:54 | 46043.5792 | 2026-01-21 13:56 | 46043.5806 | 0.0053956 | 0.0026978 | 94 | 188 | C | Wildlife | Magpie V Lines
596 |  | 251215YRAZZMGJ | W133 |  | Bells Pond CB13 - Waikakahi | 2026-01-21 08:00 | 46043.3333 | 2026-01-21 14:50 | 46043.6181 | 0.11988 | 0.0003157 | 11 | 4177 | B | Planned interruption | Notified Interruption Equipment
597 |  | 260123XZEHXGSQ | ABS W554 to CB W590 |  | Bells Pond CB2 - Tawai | 2026-01-21 14:54 | 46043.6208 | 2026-01-21 16:18 | 46043.6792 | 0.64197 | 0.0098729 | 344 | 22368 | C | ThirdPartyInterference | Car vs Pole
598 |  | 2512158ISCXBQE | T112 |  | Temuka 02 - Milford | 2026-01-21 08:30 | 46043.3542 | 2026-01-21 16:47 | 46043.6993 | 0.2527 | 0.0005453 | 19 | 8805 | B | Planned interruption | Notified Interruption Equipment
599 |  | 260123XZEHXGSQ | ABS W554 to CB W590 |  | BPD CB3602 33kV To CNR | 2026-01-21 14:54 | 46043.6208 | 2026-01-21 17:38 | 46043.7347 | 0.0047068 | 2.87e-05 | 1 | 164 | C | ThirdPartyInterference | Car vs Pole
600 |  | 260121FTVOVVYW | TO A462 |  | Bells Pond CB1 - Waihuna | 2026-01-21 17:39 | 46043.7354 | 2026-01-21 20:54 | 46043.8708 | 0.0055965 | 2.87e-05 | 1 | 195 | C | DefectiveEquipment | Replace Disc insulator
601 |  | 260123QVUQF9Q4 | Transformer - TE126 |  | Grasmere Street 12 - Selwyn Street | 2026-01-22 08:29 | 46044.3535 | 2026-01-22 09:46 | 46044.4069 | 0.12674 | 0.0039606 | 138 | 4416 | C | DefectiveEquipment | Intentional tripping sump pump fault
602 |  | 2512109GXDYGWS | B1039 - LB34 |  | Timaru 2862 - Meadows Road | 2026-01-22 08:30 | 46044.3542 | 2026-01-22 14:55 | 46044.6215 | 0.85082 | 0.0034727 | 121 | 29645 | B | Planned interruption | Planned Interruption Equipment
603 |  | 260123PGZBLLB4 | Fuses TO A445 |  | Studholme 09 - Morven | 2026-01-23 21:37 | 46045.9007 | 2026-01-23 22:22 | 46045.9319 | 0.0038745 | 8.6101e-05 | 3 | 135 | C | VegetationInZone | Remove tree from LV line
604 |  | 260124VCDFJFFE | L712 |  | Timaru 2852 - Hadlow | 2026-01-24 00:33 | 46046.0229 | 2026-01-24 03:42 | 46046.1542 | 0.76064 | 0.004305 | 150 | 26503 | C | CauseUnknown | Blown Fuses L716
605 |  | 260129XSL724RB | TMK CB9 to end |  | Temuka 09 - Waitohi | 2026-01-26 05:28 | 46048.2278 | 2026-01-26 08:14 | 46048.3431 | 1.4483 | 0.0087249 | 304 | 50464 | C | VegetationInZone | Trees on line
606 |  | 2512159QKYPFRM | T436 - T448 |  | Rangitata 02 - Arundel | 2026-01-26 09:07 | 46048.3799 | 2026-01-26 11:37 | 46048.484 | 0.04305 | 0.000287 | 10 | 1500 | B | Planned interruption | Planned Interruption Vegetation
607 |  | 251209ERPTZG2M | TOD906 |  | Temuka 08 - Temuka East | 2026-01-26 08:25 | 46048.3507 | 2026-01-26 16:33 | 46048.6896 | 0.76994 | 0.0017507 | 61 | 26827 | B | Planned interruption | Notified Interruption Equipment
608 |  | 251210JBUDCTJ4 | F166 |  | Albury ABY2742 - Cave | 2026-01-26 09:30 | 46048.3958 | 2026-01-26 16:07 | 46048.6715 | 0.21442 | 0.0005453 | 19 | 7471 | B | Planned interruption | Planned Interruption Equipment
609 |  | 251215MEJ8EEFQ | T110 |  | Temuka 02 - Milford | 2026-01-27 08:30 | 46049.3542 | 2026-01-27 16:30 | 46049.6875 | 0.054387 | 0.0001148 | 4 | 1895 | B | Planned interruption | Notified Interruption Equipment
610 |  | 251215HDJF36XI | G261 - G149 |  | Geraldine G156 - Woodbury | 2026-01-28 09:00 | 46050.375 | 2026-01-28 15:32 | 46050.6472 | 0.043452 | 0.0001148 | 4 | 1514 | B | Planned interruption | Notified Interruption Equipment
611 |  | 260203GPJLAD1C | Fuses G205 |  | Geraldine G194 - Speechley | 2026-01-29 06:46 | 46051.2819 | 2026-01-29 07:06 | 46051.2958 | 0.006314 | 0.0003157 | 11 | 220 | C | DefectiveEquipment | Unknown
612 |  | 251215HLJVPGIV | B772-02 + B772-03 |  | Timaru 2832 - Grants Road | 2026-01-29 09:00 | 46051.375 | 2026-01-29 15:03 | 46051.6271 | 0.62417 | 0.001722 | 60 | 21748 | B | Planned interruption | Planned Interruption Equipment
613 |  | 260202XPKGYCR6 | CB12 |  | Bells Pond CB12 - Ikawai | 2026-01-29 14:44 | 46051.6139 | 2026-01-29 17:19 | 46051.7215 | 0.2517 | 0.0026404 | 92 | 8770 | C | VegetationInZone | Unplanned - tree on line
614 |  | 251215FOFJBMF4 | G261 - G149 |  | Geraldine G156 - Woodbury | 2026-01-29 09:00 | 46051.375 | 2026-01-29 17:52 | 46051.7444 | 0.061074 | 0.0001148 | 4 | 2128 | B | Planned interruption | Notified Interruption Equipment
615 |  | 260203JPV8PPKH | W664 - W699 |  | Studholme 07 - Waihaorunga | 2026-01-29 19:53 | 46051.8285 | 2026-01-29 21:41 | 46051.9035 | 0.59854 | 0.022989 | 801 | 20855 | C | CauseUnknown | Unknown ( Vegetation ?)
616 |  | 2602034PXVJKP2 | F265 |  | Fairlie F380 - Fairlie Rural | 2026-02-01 21:01 | 46054.8757 | 2026-02-01 23:46 | 46054.9903 | 0.04262 | 0.0002583 | 9 | 1485 | C | DefectiveEquipment | Unknown
617 |  | 260203MXKN4225 | 0005692318ALCA9 |  | Temuka 02 - Milford | 2026-02-02 13:30 | 46055.5625 | 2026-02-02 16:50 | 46055.7014 | 0.053555 | 0.0010045 | 35 | 1866 | C | VegetationOutZone | Broken conductors across the road
618 |  | 260112SNUZPPJY | CB W515 to ABS W532 |  | Bells Pond CB13 - Waikakahi | 2026-02-02 08:00 | 46055.3333 | 2026-02-02 16:25 | 46055.684 | 0.68593 | 0.0014637 | 51 | 23900 | B | Planned interruption | Planned Interruption Equipment
619 |  | 260226ZKWO4S74 | CB T626 - LBS T775 |  | Clandeboye No 1 T613 - Rolleston Road | 2026-02-06 06:17 | 46059.2618 | 2026-02-06 07:41 | 46059.3201 | 0.36653 | 0.0053095 | 185 | 12771 | C | Wildlife | CB T626 Trip on A& B phase fault
620 |  | 260116RPSSK7QF | RMU TEW10 - LB C19 |  | North Street 12 - High Street | 2026-02-09 09:50 | 46062.4097 | 2026-02-09 15:35 | 46062.6493 | 0.038401 | 0.0001148 | 4 | 1338 | B | Planned interruption | Planned Interruption Equipment
621 |  | 260112OZXI1C31 | ABS F368 - ABS F348 |  | Fairlie F374 - Cricklewood | 2026-02-09 09:30 | 46062.3958 | 2026-02-09 15:50 | 46062.6597 | 0.65376 | 0.001722 | 60 | 22779 | B | Planned interruption | Notified Interruption Equipment
622 |  | 2601137CAGHUMP | G262 - G248 |  | Geraldine G156 - Woodbury | 2026-02-10 08:30 | 46063.3542 | 2026-02-10 16:04 | 46063.6694 | 0.12436 | 0.000287 | 10 | 4333 | B | Planned interruption | Notified Interruption Equipment
623 |  | 2601123IZMKSCI | TOC387 |  | Albury ABY2742 - Cave | 2026-02-11 10:03 | 46064.4187 | 2026-02-11 12:02 | 46064.5014 | 0.0034153 | 2.87e-05 | 1 | 119 | B | Planned interruption | Planned Interruption Equipment
624 |  | 251110LWTWSWSS | TX E295 |  | Tekapo M204 - Lakeside Drive | 2026-02-11 10:02 | 46064.4181 | 2026-02-11 12:38 | 46064.5264 | 0.0089545 | 5.74e-05 | 2 | 312 | B | Planned interruption | Planned Interruption Equipment
625 |  | 260113PCCLMNL1 | G247 - TX65 |  | Geraldine G156 - Woodbury | 2026-02-11 08:30 | 46064.3542 | 2026-02-11 15:52 | 46064.6611 | 1.0082 | 0.0023821 | 83 | 35127 | B | Planned interruption | Notified Interruption Equipment
626 |  | 2601234VTSTGQH | L536 - L1487 - B1397-02 - B1397-05 |  | Timaru 2702 - Morgans Road | 2026-02-12 09:05 | 46065.3785 | 2026-02-12 15:09 | 46065.6312 | 0.95259 | 0.0028126 | 98 | 33191 | B | Planned interruption | Planned Interruption Equipment
627 |  | 260112MQGUOY2H | Fuses F110 to the end |  | Albury ABY2742 - Cave | 2026-02-12 09:00 | 46065.375 | 2026-02-12 15:20 | 46065.6389 | 0.1854 | 0.0004879 | 17 | 6460 | B | Planned interruption | Planned Interruption Equipment
628 |  | 260226DQ9QHGCI | B275 to end |  | Timaru 2852 - Hadlow | 2026-02-12 17:05 | 46065.7118 | 2026-02-12 22:04 | 46065.9194 | 0.65129 | 0.0072898 | 254 | 22693 | C | ThirdPartyInterference | Tree on line at pole 35495
629 |  | 260217EMBYM9PE | Fuses L220 to end |  | Pleasant Point CB4 - Totara Valley | 2026-02-13 14:37 | 46066.609 | 2026-02-13 17:43 | 46066.7382 | 0.1121 | 0.0006027 | 21 | 3906 | C | DefectiveEquipment | Emergency pole replacement
630 |  | 260116RAQIGPJC | ABS L753 towards Fuses TOB1698 |  | WSS CB14 Woolworks | 2026-02-14 09:00 | 46067.375 | 2026-02-14 12:00 | 46067.5 | 0.015498 | 8.6101e-05 | 3 | 540 | B | Planned interruption | Planned Interruption Equipment
631 |  | 260215KGPIESLO | E306 |  | Tekapo M346 - Unwin Hut 33kV | 2026-02-15 07:35 | 46068.316 | 2026-02-15 09:45 | 46068.4062 | 0.030853 | 0.0002583 | 9 | 1075 | C | Lightning | Blown fuses M53 & E306
632 |  | 251120HCUP1FRK | F226 |  | Fairlie F380 - Fairlie Rural | 2026-02-16 09:00 | 46069.375 | 2026-02-16 10:55 | 46069.4549 | 0.036306 | 0.0003157 | 11 | 1265 | B | Planned interruption | Planned Interruption Equipment
633 |  | 260216YEPJJRMF | Fuses G324 |  | Geraldine G156 - Woodbury | 2026-02-16 11:53 | 46069.4951 | 2026-02-16 14:21 | 46069.5979 | 0.076457 | 0.0005166 | 18 | 2664 | C | DefectiveEquipment | Fuses G324
634 |  | 260113MSYOWZBE | TX65 - T430 - T800 |  | Geraldine G156 - Woodbury | 2026-02-18 08:30 | 46071.3542 | 2026-02-18 16:06 | 46071.6708 | 0.22799 | 0.0005453 | 19 | 7944 | B | Planned interruption | Notified Interruption Equipment
635 |  | 260119YSC4D4RC | Fuses TOA705 to end |  | Bells Pond CB2 - Tawai | 2026-02-18 08:32 | 46071.3556 | 2026-02-18 16:20 | 46071.6806 | 0.81227 | 0.0018368 | 64 | 28302 | B | Planned interruption | Notified Interruption Equipment
636 |  | 260226XUCI5LW7 | C269 cct 3 to end barrier at pole 15336 to 0007082002AL362 |  | Fairlie F383 - Fairlie Township | 2026-02-19 12:18 | 46072.5125 | 2026-02-19 17:21 | 46072.7229 | 3.8263 | 0.036765 | 1281 | 133319 | C | ThirdPartyInterference | Truck VS pole 15336
637 |  | 260113JA8ECUTP | TX65 - T430 - T800 |  | Geraldine G156 - Woodbury | 2026-02-19 08:34 | 46072.3569 | 2026-02-19 16:57 | 46072.7063 | 0.2253 | 0.0005453 | 19 | 7850 | B | Planned interruption | Notified Interruption Equipment
638 |  | 260123CSUSYKQE | Pole #877279 - W337 |  | Pareora CB4 - St Andrews | 2026-02-20 09:02 | 46073.3764 | 2026-02-20 14:21 | 46073.5979 | 0.21712 | 0.0006888 | 24 | 7565 | B | Planned interruption | Notified Interruption Equipment
639 |  | 260120WODDIM3W | HNT CB13 - RMU E46 |  | Hunt Street 13 - Clifton Terrace | 2026-02-20 09:00 | 46073.375 | 2026-02-20 14:37 | 46073.609 | 1.4218 | 0.0042189 | 147 | 49539 | B | Planned interruption | Notified Interruption Equipment
640 |  | 260203XIROAJA3 | D747-02 |  | Temuka 03 - Winchester | 2026-02-24 09:16 | 46077.3861 | 2026-02-24 13:24 | 46077.5583 | 0.092529 | 0.0003731 | 13 | 3224 | B | Planned interruption | Planned Interruption Equipment
641 |  | 2601133HEWKHHI | Pole #41735 |  | Geraldine G156 - Woodbury | 2026-02-24 08:30 | 46077.3542 | 2026-02-24 14:41 | 46077.6118 | 0.031168 | 8.6101e-05 | 3 | 1086 | B | Planned interruption | Notified Interruption Equipment
642 |  | 260120X85FH2XS | TE29-12 - TE29-13 |  | Grasmere Street 15 - Park Lane | 2026-02-24 08:30 | 46077.3542 | 2026-02-24 15:49 | 46077.659 | 0.087249 | 0.0002583 | 9 | 3040 | B | Planned interruption | Planned Interruption Equipment
643 |  | 260226PLO2E9WY | ABS T497 |  | Rangitata 13 - Rangitata Island | 2026-02-24 19:58 | 46077.8319 | 2026-02-25 00:15 | 46078.0104 | 0.44017 | 0.0019229 | 67 | 15337 | C | DefectiveEquipment | Replace red tagged POle
644 |  | 260129JUS9LYYM | L827 |  | Timaru 2852 - Hadlow | 2026-02-25 09:00 | 46078.375 | 2026-02-25 11:40 | 46078.4861 | 0.16991 | 0.0010619 | 37 | 5920 | B | Planned interruption | Planned Interruption Vegetation
645 |  | 260225XJY7JDFK | W305 Fuses |  | Studholme 01 - Otaio | 2026-02-25 11:15 | 46078.4688 | 2026-02-25 15:15 | 46078.6354 | 0.075768 | 0.0003157 | 11 | 2640 | C | Vegetation | Remove Trees from Lines P#33507
646 |  | 260113TA1XV2ZE | Pole #08363 - T419 |  | Geraldine G156 - Woodbury | 2026-02-25 08:30 | 46078.3542 | 2026-02-25 17:30 | 46078.7292 | 0.26743 | 0.000574 | 20 | 9318 | B | Planned interruption | Notified Interruption Equipment
647 |  | 260204Q7NBRM3Y | W223 |  | Studholme 08 - Mount Studholme | 2026-02-23 11:32 | 46076.4806 | 2026-02-26 | 46079 | 0.4165 | 0.0001148 | 4 | 14512 | B | Planned interruption | Planned Interruption Equipment
648 |  | 260129USZVM2VN | 11KV ABS T640 |  | Temuka 09 - Waitohi | 2026-02-26 09:00 | 46079.375 | 2026-02-26 10:25 | 46079.434 | 0.078064 | 0.00091841 | 32 | 2720 | B | Planned interruption | Notified Interruption Equipment
649 |  | 260113BOQZDNSJ | Pole #08363 - T419 |  | Geraldine G156 - Woodbury | 2026-02-26 08:30 | 46079.3542 | 2026-02-26 12:58 | 46079.5403 | 0.15383 | 0.000574 | 20 | 5360 | B | Planned interruption | Notified Interruption Equipment
650 |  | 260226FIVIGHS0 | TO A1546 |  | Studholme 09 - Morven | 2026-02-26 12:50 | 46079.5347 | 2026-02-26 16:48 | 46079.7 | 0.013661 | 5.74e-05 | 2 | 476 | C | VegetationInZone | Bark on Tx A1546
651 |  | 260227WTMEJGFU | TO A1128 |  | Studholme 02 - Glenavy | 2026-02-26 15:53 | 46079.6618 | 2026-02-26 18:13 | 46079.759 | 0.004018 | 2.87e-05 | 1 | 140 | C | ThirdPartyInterference | Replace stolen earths @ Tx A1128
652 |  | 260225HDMIKCHS | W223 |  | Studholme 08 - Mount Studholme | 2026-02-26 | 46079 | 2026-02-27 12:31 | 46080.5215 | 0.29108 | 0.0001435 | 5 | 10142 | B | Planned interruption | Planned Interruption Equipment
653 |  | 260210RVROXZUG | Links F288 with barrier at Links F419 |  | Fairlie F380 - Fairlie Rural | 2026-02-27 09:01 | 46080.3757 | 2026-02-27 14:11 | 46080.591 | 1.1477 | 0.0037023 | 129 | 39990 | B | Planned interruption | Notified Interruption Equipment
654 |  | 260203CXJ7YZRG | Fuses L128 |  | Pareora CB7 - Holmestation | 2026-02-27 08:30 | 46080.3542 | 2026-02-27 14:57 | 46080.6229 | 0.25167 | 0.0006601 | 23 | 8769 | B | Planned interruption | Planned Interruption Equipment
655 |  | 260227LJ5AEELA | Fuses F116 |  | Albury ABY2732 - Raincliff | 2026-02-27 17:09 | 46080.7146 | 2026-02-27 18:17 | 46080.7618 | 0.0078064 | 0.0001148 | 4 | 272 | C | ThirdPartyInterference | Digger Vs Lines
656 |  | 260311OCNDH8PH | Transformer - B2046 |  | Pareora CB6 - Normanby | 2026-03-01 18:37 | 46082.7757 | 2026-03-02 09:38 | 46083.4014 | 0.025859 | 2.87e-05 | 1 | 901 | C | Lightning | Possible lightning
657 |  | 2602032LY1BKX1 | TX Fuses TOD255 |  | Geraldine G194 - Speechley | 2026-03-02 10:20 | 46083.4306 | 2026-03-02 10:54 | 46083.4542 | 0.003157 | 0.0001148 | 4 | 110 | B | Planned interruption | Planned Interruption Equipment
658 |  | 260202ALHSMPFU | TOB1673 |  | Albury ABY2742 - Cave | 2026-03-02 09:11 | 46083.3826 | 2026-03-02 11:33 | 46083.4812 | 0.0040754 | 2.87e-05 | 1 | 142 | B | Planned interruption | Planned Interruption Vegetation
659 |  | 260205YX8ONXEZ | Pole #15166 |  | Fairlie F380 - Fairlie Rural | 2026-03-02 09:00 | 46083.375 | 2026-03-02 15:06 | 46083.6292 | 0.094538 | 0.0002583 | 9 | 3294 | B | Planned interruption | Notified Interruption Equipment
660 |  | 260203NWFT4DKH | ABS T647 |  | Rangitata 04 - Main South Road | 2026-03-02 10:49 | 46083.4507 | 2026-03-02 15:52 | 46083.6611 | 0.017392 | 5.74e-05 | 2 | 606 | B | Planned interruption | Planned Interruption Equipment
661 |  | 260205NOUSM1PI | ABS W191 - Links W131 |  | Studholme 02 - Glenavy | 2026-03-03 08:04 | 46084.3361 | 2026-03-03 19:52 | 46084.8278 | 0.45059 | 0.0042476 | 148 | 15700 | B | Planned interruption | Notified Interruption Equipment
662 |  | 260211OEPXEXIQ | Links L1329 |  | Pareora CB7 - Holmestation | 2026-03-04 09:00 | 46085.375 | 2026-03-04 13:45 | 46085.5729 | 0.61743 | 0.0021812 | 76 | 21513 | B | Planned interruption | Planned Interruption Vegetation
663 |  | 260126FOSCA3YH | T430 |  | Geraldine G156 - Woodbury | 2026-03-04 08:30 | 46085.3542 | 2026-03-04 17:23 | 46085.7243 | 0.22779 | 0.0005166 | 18 | 7937 | B | Planned interruption | Notified Interruption Equipment
664 |  | 260311FWSBRCFB | F207 |  | Fairlie F374 - Cricklewood | 2026-03-04 16:18 | 46085.6792 | 2026-03-04 17:42 | 46085.7375 | 0.026519 | 0.0003157 | 11 | 924 | C | DefectiveEquipment | Emergency red tag pole replacement
665 |  | 260212DKEFDXEB | Fuses TOD577 |  | Geraldine G194 - Speechley | 2026-03-05 09:03 | 46086.3771 | 2026-03-05 14:03 | 46086.5854 | 0.01722 | 5.74e-05 | 2 | 600 | B | Planned interruption | Planned Interruption Vegetation
666 |  | 2602020DHIS9AC | ABS G106 - Links G322 - ABS G104 |  | Temuka 03 - Winchester | 2026-03-05 08:37 | 46086.359 | 2026-03-05 16:00 | 46086.6667 | 0.58413 | 0.0015211 | 53 | 20353 | B | Planned interruption | Notified Interruption Equipment
667 |  | 2603057LT66BON | TO A1305 |  | Studholme 01 - Otaio | 2026-03-05 18:08 | 46086.7556 | 2026-03-05 19:10 | 46086.7986 | 0.0017794 | 2.87e-05 | 1 | 62 | C | ThirdPartyInterference | Repair stolen earths at Tx A1305
668 |  | 260212KXOAMSYA | TOA59 |  | Pareora CB4 - St Andrews | 2026-03-06 09:00 | 46087.375 | 2026-03-06 11:19 | 46087.4715 | 0.0079786 | 5.74e-05 | 2 | 278 | B | Planned interruption | Planned Interruption Vegetation
669 |  | 260205ZAQLXIY3 | ABS L175 |  | Pareora CB6 - Normanby | 2026-03-07 08:00 | 46088.3333 | 2026-03-07 16:30 | 46088.6875 | 0.13773 | 0.000287 | 10 | 4799 | B | Planned interruption | Planned Interruption Equipment
670 |  | 260211WDCAD1ZW | TOB26 |  | Pareora CB4 - St Andrews | 2026-03-09 10:10 | 46090.4236 | 2026-03-09 14:40 | 46090.6111 | 0.023132 | 8.6101e-05 | 3 | 806 | B | Planned interruption | Notified Interruption Equipment
671 |  | 260210UH4YS4JE | TE50-01 to end - LB U20 + Q44 |  | Grasmere Street 05 - Nile Street | 2026-03-09 08:02 | 46090.3347 | 2026-03-09 16:37 | 46090.6924 | 2.1882 | 0.0044198 | 154 | 76244 | B | Planned interruption | Notified Interruption Equipment
672 |  | 260312YEIDRMIS | Fuses F233 to end |  | Fairlie F380 - Fairlie Rural | 2026-03-10 07:34 | 46091.3153 | 2026-03-10 09:08 | 46091.3806 | 0.0053956 | 5.74e-05 | 2 | 188 | C | Wildlife | Bird Strike
673 |  | 2602243IXKGFQX | Fuses TOA212 |  | Studholme 08 - Mount Studholme | 2026-03-10 09:00 | 46091.375 | 2026-03-10 10:20 | 46091.4306 | 0.018368 | 0.0002296 | 8 | 640 | B | Planned interruption | Planned Interruption Vegetation
674 |  | 2602103YQTZSW8 | TE50-01 LV Main Isolator to end - CCT11 - CCT1 - LBU20 - LBQ44 |  | Grasmere Street 05 - Nile Street | 2026-03-10 08:00 | 46091.3333 | 2026-03-10 14:55 | 46091.6215 | 1.2212 | 0.0032718 | 114 | 42550 | B | Planned interruption | Notified Interruption Equipment
675 |  | 260211OODJC30N | TOB516 |  | Pareora CB7 - Holmestation | 2026-03-10 09:54 | 46091.4125 | 2026-03-10 16:05 | 46091.6701 | 0.42026 | 0.0011767 | 41 | 14643 | B | Planned interruption | Notified Interruption Equipment
676 |  | 2603111MDETYSK | L818 |  | Timaru 2852 - Hadlow | 2026-03-11 10:23 | 46092.4326 | 2026-03-11 14:21 | 46092.5979 | 0.019803 | 8.6101e-05 | 3 | 690 | C | DefectiveEquipment | Repair Jumper & replace Tx B133
677 |  | 260210X4STMOCO | TE50-14 + TE50-17 + TE50-18 to end - LBU20 |  | Grasmere Street 05 - Nile Street | 2026-03-11 08:00 | 46092.3333 | 2026-03-11 15:07 | 46092.6299 | 0.81379 | 0.0019803 | 69 | 28355 | B | Planned interruption | Notified Interruption Equipment
678 |  | 260212GBSJ7K6Q | Fuses F180 |  | Albury ABY2742 - Cave | 2026-03-11 09:00 | 46092.375 | 2026-03-11 15:12 | 46092.6333 | 0.074735 | 0.0002009 | 7 | 2604 | B | Planned interruption | Planned Interruption Vegetation
679 |  | 260218OIDMHNXP | ABS G184 to ABS GX11 - Fuses G182 |  | Geraldine G156 - Woodbury | 2026-03-11 09:00 | 46092.375 | 2026-03-11 16:29 | 46092.6868 | 0.11024 | 0.0002583 | 9 | 3841 | B | Planned interruption | Planned Interruption Equipment
680 |  | 260313AD6SZY0G | LVFeeder - A562-01 |  | Studholme 09 - Morven | 2026-03-12 11:03 | 46093.4604 | 2026-03-12 14:28 | 46093.6028 | 0.011767 | 5.74e-05 | 2 | 410 | C | ThirdPartyInterference | OH Line contact from farm equipment
681 |  | 260218SHUHBP3L | ABS G184 to ABS GX11 - Fuses G182 |  | Geraldine G156 - Woodbury | 2026-03-12 09:00 | 46093.375 | 2026-03-12 15:30 | 46093.6458 | 0.096346 | 0.0002583 | 9 | 3357 | B | Planned interruption | Planned Interruption Equipment
682 |  | 260225Y3PVQTNZ | ABS Z492 & Temp Links @ Pole #54783 |  | Twizel TVS03 - Pukaki | 2026-03-12 09:03 | 46093.3771 | 2026-03-12 16:18 | 46093.6792 | 0.56181 | 0.0012915 | 45 | 19575 | B | Planned interruption | Planned Interruption Equipment
683 |  | 260225WRBUJ1LO | RMU Z497 |  | Twizel TVS02 - Glen Lyon | 2026-03-13 09:00 | 46094.375 | 2026-03-13 11:19 | 46094.4715 | 0.027925 | 0.0002009 | 7 | 973 | B | Planned interruption | Planned Interruption Equipment
684 |  | 260313UOVDOW2A | STU CB09 |  | Studholme 09 - Morven | 2026-03-13 11:51 | 46094.4938 | 2026-03-13 12:48 | 46094.5333 | 0.56516 | 0.010275 | 358 | 19692 | C | ThirdPartyInterference | Car V Pole P#55885
685 |  | 260317XVBAWLPD | STU CB8 |  | Studholme 08 - Mount Studholme | 2026-03-14 12:39 | 46095.5271 | 2026-03-14 13:45 | 46095.5729 | 0.64593 | 0.0097868 | 341 | 22506 | C | DefectiveEquipment | RMU W373 Fault
686 |  | 2603021MNY9CMN | B871-04 |  | North Street 18 - Redruth 2 | 2026-03-15 09:00 | 46096.375 | 2026-03-15 16:46 | 46096.6986 | 0.16049 | 0.0003444 | 12 | 5592 | B | Planned interruption | Planned Interruption Equipment
687 |  | 260216KNI98SCA | Fuses T325 |  | Geraldine G194 - Speechley | 2026-03-16 09:00 | 46097.375 | 2026-03-16 12:38 | 46097.5264 | 0.11262 | 0.0005166 | 18 | 3924 | B | Planned interruption | Planned Interruption Vegetation
688 |  | 260213YUZKHT0V | ABS W221 to end |  | Studholme 08 - Mount Studholme | 2026-03-16 09:27 | 46097.3938 | 2026-03-16 13:11 | 46097.5493 | 0.19287 | 0.00086101 | 30 | 6720 | B | Planned interruption | Planned Interruption Vegetation
689 |  | 260219RNTLMCUG | Fuses TOA1505 |  | Bells Pond CB1 - Waihuna | 2026-03-16 10:34 | 46097.4403 | 2026-03-16 14:12 | 46097.5917 | 0.0062566 | 2.87e-05 | 1 | 218 | B | Planned interruption | Planned Interruption Equipment
690 |  | 260303A62Y8O3J | T108 |  | Temuka 02 - Milford | 2026-03-16 08:31 | 46097.3549 | 2026-03-16 15:00 | 46097.625 | 0.12023 | 0.0003157 | 11 | 4189 | B | Planned interruption | Notified Interruption Equipment
691 |  | 2602196JXUXFDY | Fuses TOC186 |  | Fairlie F380 - Fairlie Rural | 2026-03-17 09:00 | 46098.375 | 2026-03-17 14:43 | 46098.6132 | 0.019688 | 5.74e-05 | 2 | 686 | B | Planned interruption | Planned Interruption Equipment
692 |  | 260303YE2CKXDH | T130+Pole 01744 |  | Temuka 02 - Milford | 2026-03-17 08:00 | 46098.3333 | 2026-03-17 16:39 | 46098.6937 | 0.1569 | 0.0003444 | 12 | 5467 | B | Planned interruption | Notified Interruption Equipment
693 |  | 260318RE5WKSPZ | TO D684 |  | Clandeboye No 1 T613 - Rolleston Road | 2026-03-17 20:49 | 46098.8674 | 2026-03-18 08:30 | 46099.3542 | 0.020119 | 2.87e-05 | 1 | 701 | C | DefectiveEquipment | Blown Tx Fuses
694 |  | 260219TAYPAAPF | TX B919-01 to end - LB6 |  | Timaru 2702 - Morgans Road | 2026-03-18 09:00 | 46099.375 | 2026-03-18 13:44 | 46099.5722 | 0.35714 | 0.0014063 | 49 | 12444 | B | Planned interruption | Planned Interruption Equipment
695 |  | 260303C1JYU2Y3 | T130+Pole 01744 |  | Temuka 02 - Milford | 2026-03-18 08:00 | 46099.3333 | 2026-03-18 14:34 | 46099.6069 | 0.13047 | 0.0003444 | 12 | 4546 | B | Planned interruption | Notified Interruption Equipment
696 |  | 260318VVEMMRLD | STU CB8 to end |  | Studholme 08 - Mount Studholme | 2026-03-18 15:18 | 46099.6375 | 2026-03-18 15:38 | 46099.6514 | 0.19574 | 0.0097868 | 341 | 6820 | C | ThirdPartyInterference | Digger strike
697 |  | 260318J1KY79H0 | M355 |  | Tekapo M346 - Unwin Hut 33kV | 2026-03-18 12:37 | 46099.5257 | 2026-03-18 17:22 | 46099.7236 | 0.049077 | 0.0001722 | 6 | 1710 | C | DefectiveEquipment | Broken King Bolt at Pole #53668
698 |  | 260224TGUYJNPA | Tx E1 |  | TVS11 - Urban No2 | 2026-03-19 09:00 | 46100.375 | 2026-03-19 11:09 | 46100.4646 | 0.059237 | 0.0004592 | 16 | 2064 | B | Planned interruption | Planned Interruption Equipment
699 |  | 260224FSVHPPRF | Fuses L1248 |  | Pareora CB4 - St Andrews | 2026-03-19 09:00 | 46100.375 | 2026-03-19 14:53 | 46100.6201 | 0.081049 | 0.0002296 | 8 | 2824 | B | Planned interruption | Planned Interruption Vegetation
700 |  | 260303QXRJTTN3 | T125 |  | Temuka 02 - Milford | 2026-03-19 08:00 | 46100.3333 | 2026-03-19 15:09 | 46100.6312 | 0.048618 | 0.0001148 | 4 | 1694 | B | Planned interruption | Notified Interruption Equipment
701 |  | 260205KVUI64LF | W138 |  | Bells Pond CB13 - Waikakahi | 2026-03-19 08:00 | 46100.3333 | 2026-03-19 17:49 | 46100.7424 | 0.26751 | 0.0004879 | 17 | 9321 | B | Planned interruption | Notified Interruption Equipment
702 |  | 260218BQVI9JHD | ABS G186 to ABS GX11 - Fuses G182 - ABS G153 |  | Geraldine G156 - Woodbury | 2026-03-24 09:00 | 46105.375 | 2026-03-24 17:10 | 46105.7153 | 0.27885 | 0.0006888 | 24 | 9716 | B | Planned interruption | Planned Interruption Equipment
703 |  | 2602245POE3GXQ | LBS M441 |  | Haldon-Lilybank M86 - Haldon-Lilybank | 2026-03-24 09:00 | 46105.375 | 2026-03-24 15:56 | 46105.6639 | 0.45369 | 0.0010906 | 38 | 15808 | B | Planned interruption | Planned Interruption Equipment
704 |  | 260218QD36CK2X | ABS G186 to ABS GX11 - Fuses G182 - ABS G153 |  | Geraldine G156 - Woodbury | 2026-03-25 09:00 | 46106.375 | 2026-03-25 17:00 | 46106.7083 | 0.2806 | 0.0006888 | 24 | 9777 | B | Planned interruption | Planned Interruption Equipment
705 |  | 260326SVN1AXUG | Fuses TOB1035 |  | Pleasant Point CB1 - Waitawa | 2026-03-26 08:58 | 46107.3736 | 2026-03-26 10:57 | 46107.4563 | 0.0034153 | 2.87e-05 | 1 | 119 | C | DefectiveEquipment | Replace crossarm
706 |  | 260303G6VQMBOY | ABS L836 |  | Timaru 2852 - Hadlow | 2026-03-26 09:00 | 46107.375 | 2026-03-26 13:07 | 46107.5465 | 0.36154 | 0.0014637 | 51 | 12597 | B | Planned interruption | Planned Interruption Equipment
707 |  | 260310GP1QSDMY | TX B197-04 |  | Timaru 2832 - Grants Road | 2026-03-26 09:00 | 46107.375 | 2026-03-26 13:50 | 46107.5764 | 0.13317 | 0.0004592 | 16 | 4640 | B | Planned interruption | Planned Interruption Equipment
708 |  | 2603273RMAVMFN | Fuses TO A133 |  | Studholme 01 - Otaio | 2026-03-27 11:40 | 46108.4861 | 2026-03-27 14:20 | 46108.5972 | 0.13799 | 0.0013202 | 46 | 4808 | C | DefectiveEquipment | Faulty TX A133
709 |  | 260218U9R9DU0Q | ABS G186 - Fuses G181 - ABS G153 |  | Geraldine G156 - Woodbury | 2026-03-27 09:00 | 46108.375 | 2026-03-27 14:46 | 46108.6153 | 0.39451 | 0.0011767 | 41 | 13746 | B | Planned interruption | Planned Interruption Equipment
710 |  | 2603307WNNVI6Y | F252 |  | Fairlie F380 - Fairlie Rural | 2026-03-27 20:02 | 46108.8347 | 2026-03-27 23:00 | 46108.9583 | 0.025543 | 0.0001435 | 5 | 890 | C | CauseUnknown | 2 x Blown DDOs
711 |  | 260330CUCKPD7W | D911 |  | Temuka 07 - Rangitata | 2026-03-30 13:20 | 46111.5556 | 2026-03-30 13:30 | 46111.5625 | 0.000287 | 2.87e-05 | 1 | 10 | C | DefectiveEquipment | HV Fuse Resizing
712 |  | 260331F0PI38SI | Before T4976 |  | Rangitata 13 - Rangitata Island | 2026-03-31 08:21 | 46112.3479 | 2026-03-31 08:59 | 46112.3743 | 0.068823 | 0.0018655 | 65 | 2398 | C | HumanError | Isolation of cancelled job
713 |  | 260226PUYGBTBX | T109 |  | Temuka 02 - Milford | 2026-03-31 08:33 | 46112.3562 | 2026-03-31 16:32 | 46112.6889 | 0.13848 | 0.0003157 | 11 | 4825 | B | Planned interruption | Notified Interruption Equipment
714
1577
1578 |  | ¹ Extend table as necessary to disclose information for all individual interruptions
1579