## CoverSheet
EDB Information Disclosure Requirements
Information Templates
for
Schedules 11a–13
| Company Name | Alpine Energy Limited
| Disclosure Date | 2020-03-31
| AMP Planning Period Start Date (first day) | 2020-04-01
Templates for Schedules 11a–13 (Asset Management Plan)
Template Version 4.1. Prepared 21 December 2017

## TOC
Table of Contents
Information disclosure asset management plan schedules
Schedule | Schedule name
11a | REPORT ON FORECAST CAPITAL EXPENDITURE
11b | REPORT ON FORECAST OPERATIONAL EXPENDITURE
12a | REPORT ON ASSET CONDITION
12b | REPORT ON FORECAST CAPACITY
12c | REPORT ON FORECAST NETWORK DEMAND
12d | REPORT FORECAST INTERRUPTIONS AND DURATION
13 | REPORT ON ASSET MANAGEMENT MATURITY

## Instructions
Disclosure Template Instructions
These templates have been prepared for use by EDBs when making disclosures under subclauses 2.6.1(1)(d), 2.6.1(1)(e), 2.6.1(2), 2.6.5(6), 2.6.6(1) and 2.6.6(2) of the Electricity Distribution Information Disclosure Determination 2012. The EDB may include a completed Schedule 13: Report on Asset Management Maturity table with its disclosures made under subclause 2.6.6(1) and 2.6.6(2), but this is not required. Schedule 13 tables that are not completed should be removed from disclosures made under subclause 2.6.6(1) and 2.6.6(2).
Company Name and Dates
To prepare the templates for disclosure, the supplier's company name should be entered in cell C8, the date of the first day of the 10 year planning period should be entered in cell C12, and the date on which the information is disclosed should be entered in cell C10 of the CoverSheet worksheet.
The cell C12 entry (planning period start date) is used to calculate disclosure years in the column headings that show above some of the tables. It is also used to calculate the AMP planning period dates in the template title blocks (the title blocks are the light green shaded areas at the top of each template). The cell C8 entry (company name ) is used in the template title blocks. Dates should be entered in day/month/year order (Example -"1 April 2013").
Data Entry Cells and Calculated Cells
Data entered into this workbook may be entered only into the data entry cells. Data entry cells are the bordered, unshaded areas (white cells) in each template. Under no circumstances should data be entered into the workbook outside a data entry cell.
In some cases, where the information for disclosure is able to be ascertained from disclosures elsewhere in the workbook, such information is disclosed in a calculated cell.
Validation Settings on Data Entry Cells
To maintain a consistency of format and to guard against errors in data entry, some data entry cells test entries for validity and accept only a limited range of values. For example, entries may be limited to a list of category names or to values between 0% and 100%. Where this occurs, a validation message will appear when data is being entered.
Conditional Formatting Settings on Data Entry Cells
Schedule 12a columns G to K contains conditional formatting. The cells will change colour if the row totals do not add to 100%.
Inserting Additional Rows
The templates for schedules 11a, 12b and 12c may require additional rows to be inserted in tables marked 'include additional rows if needed'.
Additional rows must not be inserted directly above the first row or below the last row of a table. This is to ensure that entries made in the new row are included in the totals. For schedule 12b the formula for column J (Utilisation of Installed Firm Capacity %) will need to be copied into the inserted row(s). Column A schedule references should not be entered in additional rows.
Schedule References
The references labelled 'sch ref' in the leftmost column of each template are consistent with the row references in the Electricity Distribution ID Determination 2012 (as issued on 21 December 2017). They provide a common reference between the rows in the determination and the template.
Description of Calculation References
Calculation cell formulas contain links to other cells within the same template or elsewhere in the workbook. Key cell references are described in a column to the right of each template. These descriptions are provided to assist data entry. Cell references refer to the row of the template and not the schedule reference.

## S11a.Capex Forecast
[13 empty] | Company Name | Alpine Energy Limited
[13 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
SCHEDULE 11a: REPORT ON FORECAST CAPITAL EXPENDITURE
This schedule requires a breakdown of forecast expenditure on assets for the current disclosure year and a 10 year planning period. The forecasts should be consistent with the supporting information set out in the AMP. The forecast is to be expressed in both constant price and nominal dollar terms. Also required is a forecast of the value of commissioned assets (i.e., the value of RAB additions) EDBs must provide explanatory comment on the difference between constant price and nominal dollar forecasts of expenditure on assets in Schedule 14a (Mandatory Explanatory Notes). This information is not part of audited disclosure information.
sch ref
7 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
9 | 11a(i): Expenditure on Assets Forecast |  |  |  |  | 2020-03-31: $000 (in nominal dollars)
10 |  |  |  | Consumer connection |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
11 |  |  |  | System growth |  | 1072 | 1557 | 2601 | 800 | 800 | 600 | 1300 | 1300 | 1300 | 1300 | 2800
12 |  |  |  | Asset replacement and renewal |  | 8045 | 10992 | 10699 | 13100 | 12715 | 9355 | 10595 | 10095 | 11475 | 10245 | 11070
13 |  |  |  | Asset relocations |  | 350 | 620 | 500 | 500 | 500 | 500 | 1000 | 1000 | 1000 | 1000 | 0
14 |  |  |  | Reliability, safety and environment:
15 |  |  |  | Quality of supply |  | 626 | 580 | 436 | 532 | 528 | 528 | 716 | 741 | 729 | 680 | 680
16 |  |  |  | Legislative and regulatory |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 |  |  |  | Other reliability, safety and environment |  | 765 | 835 | 630 | 512 | 485 | 210 | 470 | 175 | 150 | 500 | 120
18 |  |  |  | Total reliability, safety and environment |  | 1391 | 1415 | 1066 | 1044 | 1013 | 738 | 1186 | 916 | 879 | 1180 | 800
19 |  |  | Expenditure on network assets |  |  | 12858 | 16584 | 16866 | 17444 | 17028 | 13193 | 16081 | 15311 | 16654 | 15725 | 16670
20 |  |  |  | Expenditure on non-network assets |  | 2842 | 1538.9342 | 688.8503 | 626.0425 | 737.6418 | 793.4805 | 669.9149 | 676.3164 | 613.9523 | 759.777 | 696.2984
21 |  |  | Expenditure on assets |  |  | 15700 | 18122.9342 | 17554.8503 | 18070.0425 | 17765.6418 | 13986.4805 | 16750.9149 | 15987.3164 | 17267.9523 | 16484.777 | 17366.2984
22
23 |  | plus |  | Cost of financing
24 |  | less |  | Value of capital contributions |  | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000
25 |  | plus |  | Value of vested assets
26
27 |  |  | Capital expenditure forecast |  |  | 13700 | 16122.9342 | 15554.8503 | 16070.0425 | 15765.6418 | 11986.4805 | 14750.9149 | 13987.3164 | 15267.9523 | 14484.777 | 15366.2984
28
29 |  |  |  | Assets commissioned |  | 10494 | 17328.9342 | 12348.8503 | 16466.0425 | 12559.6418 | 13192.4805 | 11544.9149 | 15193.3164 | 12061.9523 | 15690.777 | 12160.2984
30 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
31 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
32 | [5 empty] | 2020-03-31: $000 (in constant prices)
33 |  |  |  | Consumer connection |  | 2000 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | 1960.7843 | from row 76
34 |  |  |  | System growth |  | 1072 | 1673.5294 | 3187.2549 | 980.3922 | 882.3529 | 686.2745 | 1274.5098 | 1274.5098 | 1274.5098 | 1274.5098 | 2745.098 | from row 87
35 |  |  |  | Asset replacement and renewal |  | 8045 | 11247.0588 | 11959.8039 | 12490.1961 | 12171.5686 | 9171.5686 | 10387.2549 | 9897.0588 | 11250 | 10044.1176 | 10852.9412 | from row 101
36 |  |  |  | Asset relocations |  | 350 | 607.8431 | 490.1961 | 490.1961 | 490.1961 | 490.1961 | 980.3922 | 980.3922 | 980.3922 | 980.3922 | 0 | from row 113
37 |  |  |  | Reliability, safety and environment:
38 |  |  |  | Quality of supply |  | 626 | 784.3137 | 643.1373 | 737.2549 | 733.3333 | 733.3333 | 701.9608 | 726.4706 | 714.7059 | 666.6667 | 666.6667 | from row 126
39 |  |  |  | Legislative and regulatory |  | 2020-03-31: 0; 2021-03-31: 0; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0 | from row 139
40 |  |  |  | Other reliability, safety and environment |  | 765 | 818.6275 | 617.6471 | 501.9608 | 475.4902 | 205.8824 | 460.7843 | 171.5686 | 147.0588 | 490.1961 | 117.6471 | from row 154
41 |  |  |  | Total reliability, safety and environment |  | 1391 | 1602.9412 | 1260.7843 | 1239.2157 | 1208.8235 | 939.2157 | 1162.7451 | 898.0392 | 861.7647 | 1156.8627 | 784.3137
42 |  |  | Expenditure on network assets |  |  | 12858 | 17092.1569 | 18858.8235 | 17160.7843 | 16713.7255 | 13248.0392 | 15765.6863 | 15010.7843 | 16327.451 | 15416.6667 | 16343.1373
43 |  |  |  | Expenditure on non-network assets |  | 2842 | 2058.6765 | 1116.516 | 563.0125 | 671.449 | 725.1721 | 656.7793 | 663.0553 | 601.914 | 744.8794 | 682.6455 | from row 182
44 |  |  | Expenditure on assets |  |  | 15700 | 19150.8333 | 19975.3396 | 17723.7968 | 17385.1745 | 13973.2114 | 16422.4656 | 15673.8396 | 16929.365 | 16161.546 | 17025.7827
45
46 |  | Subcomponents of expenditure on assets (where known)
47 |  |  |  | Energy efficiency and demand side management, reduction of energy losses
48 |  |  |  | Overhead to underground conversion
49 |  |  |  | Research and development
50
51 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
52 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
53 |  | Difference between nominal and constant price forecasts |  |  |  | 2020-03-31: $000
54 |  |  |  | Consumer connection |  | 0 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157 | 39.2157
55 |  |  |  | System growth |  | 0 | -116.5294 | -586.2549 | -180.3922 | -82.3529 | -86.2745 | 25.4902 | 25.4902 | 25.4902 | 25.4902 | 54.902
56 |  |  |  | Asset replacement and renewal |  | 0 | -255.0588 | -1260.8039 | 609.8039 | 543.4314 | 183.4314 | 207.7451 | 197.9412 | 225 | 200.8824 | 217.0588
57 |  |  |  | Asset relocations |  | 0 | 12.1569 | 9.8039 | 9.8039 | 9.8039 | 9.8039 | 19.6078 | 19.6078 | 19.6078 | 19.6078 | 0
58 |  |  |  | Reliability, safety and environment:
59 |  |  |  | Quality of supply |  | 0 | -204.3137 | -207.1373 | -205.2549 | -205.3333 | -205.3333 | 14.0392 | 14.5294 | 14.2941 | 13.3333 | 13.3333
60 |  |  |  | Legislative and regulatory |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 |  |  |  | Other reliability, safety and environment |  | 0 | 16.3725 | 12.3529 | 10.0392 | 9.5098 | 4.1176 | 9.2157 | 3.4314 | 2.9412 | 9.8039 | 2.3529
62 |  |  |  | Total reliability, safety and environment |  | 0 | -187.9412 | -194.7843 | -195.2157 | -195.8235 | -201.2157 | 23.2549 | 17.9608 | 17.2353 | 23.1373 | 15.6863
63 |  |  | Expenditure on network assets |  |  | 0 | -508.1569 | -1992.8235 | 283.2157 | 314.2745 | -55.0392 | 315.3137 | 300.2157 | 326.549 | 308.3333 | 326.8627
64 |  |  |  | Expenditure on non-network assets |  | 0 | -519.7423 | -427.6657 | 63.0299 | 66.1928 | 68.3083 | 13.1356 | 13.2611 | 12.0383 | 14.8976 | 13.6529
65 |  |  | Expenditure on assets |  |  | 0 | -1027.8992 | -2420.4892 | 346.2456 | 380.4673 | 13.2691 | 328.4493 | 313.4768 | 338.5873 | 323.2309 | 340.5157
66 | [5 empty] | 2020-03-31: Current Year CY
67 | [5 empty] | 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
68 | 11a(ii): Consumer Connection |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
69 |  |  |  | Consumer types defined by EDB* |  | 2020-03-31: $000 (in constant prices)
70 |  |  |  | Low User Charge |  | 2020-03-31: 100; 2021-03-31: 98.0392; 2022-03-31: 98.0392; 2023-03-31: 98.0392; 2024-03-31: 98.0392; 2025-03-31: 98.0392
71 |  |  |  | 015 |  | 2020-03-31: 280; 2021-03-31: 274.5098; 2022-03-31: 274.5098; 2023-03-31: 274.5098; 2024-03-31: 274.5098; 2025-03-31: 274.5098
72 |  |  |  | 360 |  | 2020-03-31: 240; 2021-03-31: 235.2941; 2022-03-31: 235.2941; 2023-03-31: 235.2941; 2024-03-31: 235.2941; 2025-03-31: 235.2941
73 |  |  |  | Assessed |  | 2020-03-31: 460; 2021-03-31: 450.9804; 2022-03-31: 450.9804; 2023-03-31: 450.9804; 2024-03-31: 450.9804; 2025-03-31: 450.9804
74 |  |  |  | TOU400 |  | 2020-03-31: 920; 2021-03-31: 901.9608; 2022-03-31: 901.9608; 2023-03-31: 901.9608; 2024-03-31: 901.9608; 2025-03-31: 901.9608
75 |  |  |  | *include additional rows if needed
76 |  |  | Consumer connection expenditure |  |  | 2020-03-31: 2000; 2021-03-31: 1960.7843; 2022-03-31: 1960.7843; 2023-03-31: 1960.7843; 2024-03-31: 1960.7843; 2025-03-31: 1960.7843 | to row 33
77 |  | less |  | Capital contributions funding consumer connection |  | 2020-03-31: 1500; 2021-03-31: 1500; 2022-03-31: 1500; 2023-03-31: 1500; 2024-03-31: 1500; 2025-03-31: 1500
78 |  |  | Consumer connection less capital contributions |  |  | 2020-03-31: 500; 2021-03-31: 460.7843; 2022-03-31: 460.7843; 2023-03-31: 460.7843; 2024-03-31: 460.7843; 2025-03-31: 460.7843
79 | 11a(iii): System Growth
80 |  |  |  | Subtransmission |  | 2020-03-31: 0
81 |  |  |  | Zone substations |  | 2020-03-31: 2; 2021-03-31: 1.9608; 2022-03-31: 1961.7647; 2023-03-31: 196.0784; 2024-03-31: 196.0784; 2025-03-31: 0
82 |  |  |  | Distribution and LV lines |  | 2020-03-31: 265; 2021-03-31: 563.7255; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0
83 |  |  |  | Distribution and LV cables |  | 2020-03-31: 300; 2021-03-31: 294.1176; 2022-03-31: 294.1176; 2023-03-31: 294.1176; 2024-03-31: 294.1176; 2025-03-31: 294.1176
84 |  |  |  | Distribution substations and transformers |  | 2020-03-31: 120; 2021-03-31: 147.0588; 2022-03-31: 147.0588; 2023-03-31: 147.0588; 2024-03-31: 147.0588; 2025-03-31: 147.0588
85 |  |  |  | Distribution switchgear |  | 2020-03-31: 235; 2021-03-31: 147.0588; 2022-03-31: 147.0588; 2023-03-31: 147.0588; 2024-03-31: 147.0588; 2025-03-31: 147.0588
86 |  |  |  | Other network assets |  | 2020-03-31: 150; 2021-03-31: 372.549; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0
87 |  |  | System growth expenditure |  |  | 2020-03-31: 1072; 2021-03-31: 1526.4706; 2022-03-31: 2550; 2023-03-31: 784.3137; 2024-03-31: 784.3137; 2025-03-31: 588.2353 | to row 34
88 |  | less |  | Capital contributions funding system growth |  | 2020-03-31: 300; 2021-03-31: 300; 2022-03-31: 300; 2023-03-31: 300; 2024-03-31: 300; 2025-03-31: 300
89 |  |  | System growth less capital contributions |  |  | 2020-03-31: 772; 2021-03-31: 1226.4706; 2022-03-31: 2250; 2023-03-31: 484.3137; 2024-03-31: 484.3137; 2025-03-31: 288.2353
90
91 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
92 |  |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
93 | 11a(iv): Asset Replacement and Renewal |  |  |  |  | 2020-03-31: $000 (in constant prices)
94 |  |  |  | Subtransmission |  | 2020-03-31: 100; 2021-03-31: 294.1176; 2022-03-31: 225.4902; 2023-03-31: 29.4118; 2024-03-31: 0; 2025-03-31: 0
95 |  |  |  | Zone substations |  | 2020-03-31: 555; 2021-03-31: 1568.6275; 2022-03-31: 1303.9216; 2023-03-31: 3382.3529; 2024-03-31: 3137.2549; 2025-03-31: 696.0784
96 |  |  |  | Distribution and LV lines |  | 2020-03-31: 3870; 2021-03-31: 5711.7647; 2022-03-31: 5433.3333; 2023-03-31: 5387.2549; 2024-03-31: 5990.1961; 2025-03-31: 5539.2157
97 |  |  |  | Distribution and LV cables |  | 2020-03-31: 700; 2021-03-31: 981.3725; 2022-03-31: 637.2549; 2023-03-31: 1382.3529; 2024-03-31: 686.2745; 2025-03-31: 735.2941
98 |  |  |  | Distribution substations and transformers |  | 2020-03-31: 1770; 2021-03-31: 1617.6471; 2022-03-31: 1666.6667; 2023-03-31: 1666.6667; 2024-03-31: 1666.6667; 2025-03-31: 1666.6667
99 |  |  |  | Distribution switchgear |  | 2020-03-31: 130; 2021-03-31: 98.0392; 2022-03-31: 49.0196; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0
100 |  |  |  | Other network assets |  | 2020-03-31: 920; 2021-03-31: 504.902; 2022-03-31: 1173.5294; 2023-03-31: 995.098; 2024-03-31: 985.2941; 2025-03-31: 534.3137
101 |  |  | Asset replacement and renewal expenditure |  |  | 2020-03-31: 8045; 2021-03-31: 10776.4706; 2022-03-31: 10489.2157; 2023-03-31: 12843.1373; 2024-03-31: 12465.6863; 2025-03-31: 9171.5686 | to row 35
102 |  | less |  | Capital contributions funding asset replacement and renewal |  | 2020-03-31: 200; 2021-03-31: 200; 2022-03-31: 200; 2023-03-31: 200; 2024-03-31: 200; 2025-03-31: 200
103 |  |  | Asset replacement and renewal less capital contributions |  |  | 2020-03-31: 7845; 2021-03-31: 10576.4706; 2022-03-31: 10289.2157; 2023-03-31: 12643.1373; 2024-03-31: 12265.6863; 2025-03-31: 8971.5686
104
105 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
106 |  |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
107 | 11a(v): Asset Relocations
108 |  |  |  | Project or programme* |  | 2020-03-31: $000 (in constant prices)
109 |  |  |  | Customer requested relocations |  | 2020-03-31: 350; 2021-03-31: 607.8431; 2022-03-31: 490.1961; 2023-03-31: 490.1961; 2024-03-31: 490.1961; 2025-03-31: 490.1961
110 |  |  |  | [Description of material project or programme]
111 |  |  |  | [Description of material project or programme]
112 |  |  |  | [Description of material project or programme]
113 |  |  |  | [Description of material project or programme]
114 |  |  |  | *include additional rows if needed
115 |  |  |  | All other project or programmes - asset relocations
116 |  |  | Asset relocations expenditure |  |  | 2020-03-31: 350; 2021-03-31: 607.8431; 2022-03-31: 490.1961; 2023-03-31: 490.1961; 2024-03-31: 490.1961; 2025-03-31: 490.1961 | to row 36
117 |  | less |  | Capital contributions funding asset relocations
118 |  |  | Asset relocations less capital contributions |  |  | 2020-03-31: 350; 2021-03-31: 607.8431; 2022-03-31: 490.1961; 2023-03-31: 490.1961; 2024-03-31: 490.1961; 2025-03-31: 490.1961
119
120 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
121 |  |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
122 | 11a(vi): Quality of Supply
123 |  |  |  | Project or programme* |  | 2020-03-31: $000 (in constant prices)
124 |  |  |  | New ABS & automated devices |  | 2020-03-31: 120; 2021-03-31: 98.0392; 2022-03-31: 98.0392; 2023-03-31: 98.0392; 2024-03-31: 98.0392; 2025-03-31: 98.0392
125 |  |  |  | New RMUs |  | 2020-03-31: 100; 2021-03-31: 98.0392; 2022-03-31: 98.0392; 2023-03-31: 98.0392; 2024-03-31: 98.0392; 2025-03-31: 98.0392
126 |  |  |  | New Reclosers |  | 2020-03-31: 300; 2021-03-31: 98.0392; 2022-03-31: 98.0392; 2023-03-31: 98.0392; 2024-03-31: 98.0392; 2025-03-31: 98.0392
|  |  |  | New Comms site |  | 2021-03-31: 78.4314
127 |  |  |  | AMG upgrade |  | 2021-03-31: 147.0588
128 |  |  |  | SCADA pole top automation |  | 2020-03-31: 50; 2021-03-31: 49.0196; 2022-03-31: 98.0392; 2023-03-31: 98.0392; 2024-03-31: 98.0392; 2025-03-31: 98.0392
129 |  |  |  | *include additional rows if needed |  | 2020-03-31: 0
130 |  |  |  | All other projects or programmes - quality of supply |  | 2020-03-31: 56; 2022-03-31: 35.2941; 2023-03-31: 129.4118; 2024-03-31: 125.4902; 2025-03-31: 125.4902
131 |  |  | Quality of supply expenditure |  |  | 2020-03-31: 626; 2021-03-31: 568.6275; 2022-03-31: 427.451; 2023-03-31: 521.5686; 2024-03-31: 517.6471; 2025-03-31: 517.6471 | to row 38
132 |  | less |  | Capital contributions funding quality of supply
133 |  |  | Quality of supply less capital contributions |  |  | 2020-03-31: 626; 2021-03-31: 568.6275; 2022-03-31: 427.451; 2023-03-31: 521.5686; 2024-03-31: 517.6471; 2025-03-31: 517.6471
134
135 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
136 |  |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
137 | 11a(vii): Legislative and Regulatory
138 |  |  |  | Project or programme* |  | 2020-03-31: $000 (in constant prices)
139 |  |  |  | [Description of material project or programme]
140 |  |  |  | [Description of material project or programme]
141 |  |  |  | [Description of material project or programme]
142 |  |  |  | [Description of material project or programme]
143 |  |  |  | [Description of material project or programme]
144 |  |  |  | *include additional rows if needed
145 |  |  |  | All other projects or programmes - legislative and regulatory
146 |  |  | Legislative and regulatory expenditure |  |  | 2020-03-31: 0; 2021-03-31: 0; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0 | to row 39
147 |  | less |  | Capital contributions funding legislative and regulatory
148 |  |  | Legislative and regulatory less capital contributions |  |  | 2020-03-31: 0; 2021-03-31: 0; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 0
149
150 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
151 | 11a(viii): Other Reliability, Safety and Environment |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
152 |  |  |  | Project or programme* |  | 2020-03-31: $000 (in constant prices)
153 |  |  |  | Abloy locks |  | 2020-03-31: 100
154 |  |  |  | SCADA Mater station module |  | 2020-03-31: 50
155 |  |  |  | [Description of material project or programme]
156 |  |  |  | [Description of material project or programme]
157 |  |  |  | [Description of material project or programme]
158 |  |  |  | *include additional rows if needed
159 |  |  |  | All other projects or programmes - other reliability, safety and environment |  | 2020-03-31: 615; 2021-03-31: 818.6275; 2022-03-31: 617.6471; 2023-03-31: 501.9608; 2024-03-31: 475.4902; 2025-03-31: 205.8824
160 |  |  | Other reliability, safety and environment expenditure |  |  | 2020-03-31: 765; 2021-03-31: 818.6275; 2022-03-31: 617.6471; 2023-03-31: 501.9608; 2024-03-31: 475.4902; 2025-03-31: 205.8824 | to row 40
161 |  | less |  | Capital contributions funding other reliability, safety and environment
162 |  |  | Other reliability, safety and environment less capital contributions |  |  | 2020-03-31: 765; 2021-03-31: 818.6275; 2022-03-31: 617.6471; 2023-03-31: 501.9608; 2024-03-31: 475.4902; 2025-03-31: 205.8824
163
164 | [5 empty] | 2020-03-31: Current Year CY; 2021-03-31: CY+1; 2022-03-31: CY+2; 2023-03-31: CY+3; 2024-03-31: CY+4; 2025-03-31: CY+5
165 |  |  |  |  | for year ended | 2020-03-31: 2020-03-31; 2021-03-31: 2021-03-31; 2022-03-31: 2022-03-31; 2023-03-31: 2023-03-31; 2024-03-31: 2024-03-31; 2025-03-31: 2025-03-31
166 | 11a(ix): Non-Network Assets
167 |  | Routine expenditure
168 |  |  |  | Project or programme* |  | 2020-03-31: $000 (in constant prices)
169 |  |  |  | IT |  | 2020-03-31: 957; 2021-03-31: 649.299; 2022-03-31: 620.3655; 2023-03-31: 430.2406; 2024-03-31: 473.583; 2025-03-31: 396.0396
170 |  |  |  | Equipment |  | 2020-03-31: 615; 2021-03-31: 49.98; 2022-03-31: 54.978; 2023-03-31: 183.5266; 2024-03-31: 187.1967; 2025-03-31: 190.9412
171 |  |  |  | Vehicles |  | 2020-03-31: 170; 2021-03-31: 167.58; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 62.3986; 2025-03-31: 127.2942
172 |  |  |  | [Description of material project or programme]
173 |  |  |  | [Description of material project or programme]
174 |  |  |  | *include additional rows if needed
175 |  |  |  | All other projects or programmes - routine expenditure
176 |  |  | Routine expenditure |  |  | 2020-03-31: 1742; 2021-03-31: 866.859; 2022-03-31: 675.3435; 2023-03-31: 613.7671; 2024-03-31: 723.1783; 2025-03-31: 714.275
177 |  | Atypical expenditure
178 |  |  |  | Project or programme*
179 |  |  |  | Property |  | 2020-03-31: 1100; 2021-03-31: 641.9; 2025-03-31: 63.6471
180 |  |  |  | [Description of material project or programme]
181 |  |  |  | [Description of material project or programme]
182 |  |  |  | [Description of material project or programme]
183 |  |  |  | [Description of material project or programme]
184 |  |  |  | *include additional rows if needed
185 |  |  |  | All other projects or programmes - atypical expenditure
186 |  |  | Atypical expenditure |  |  | 2020-03-31: 1100; 2021-03-31: 641.9; 2022-03-31: 0; 2023-03-31: 0; 2024-03-31: 0; 2025-03-31: 63.6471
187
188 |  |  | Expenditure on non-network assets |  |  | 2020-03-31: 2842; 2021-03-31: 1508.759; 2022-03-31: 675.3435; 2023-03-31: 613.7671; 2024-03-31: 723.1783; 2025-03-31: 777.922 | to row 43

## S11b.Opex Forecast
[13 empty] | Company Name | Alpine Energy Limited
[13 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
SCHEDULE 11b: REPORT ON FORECAST OPERATIONAL EXPENDITURE
This schedule requires a breakdown of forecast operational expenditure for the disclosure year and a 10 year planning period. The forecasts should be consistent with the supporting information set out in the AMP. The forecast is to be expressed in both constant price and nominal dollar terms. EDBs must provide explanatory comment on the difference between constant price and nominal dollar operational expenditure forecasts in Schedule 14a (Mandatory Explanatory Notes). This information is not part of audited disclosure information.
sch ref
7 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
8 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
9 |  | Operational Expenditure Forecast |  |  |  | 2020-03-31: $000 (in nominal dollars)
10 |  |  |  | Service interruptions and emergencies |  | 1785 | 2142 | 2184.84 | 2228.5368 | 2273.1075 | 2318.5697 | 2364.9411 | 2412.2399 | 2460.4847 | 2509.6944 | 2559.8883
11 |  |  |  | Vegetation management |  | 816 | 848.64 | 865.6128 | 882.9251 | 900.5836 | 918.5952 | 936.9671 | 955.7065 | 974.8206 | 994.317 | 1014.2034
12 |  |  |  | Routine and corrective maintenance and inspection |  | 2754 | 3060 | 3121.2 | 3183.624 | 3247.2965 | 3312.2424 | 3378.4873 | 3446.057 | 3514.9781 | 3585.2777 | 3656.9833
13 |  |  |  | Asset replacement and renewal |  | 714 | 306 | 312.12 | 318.3624 | 324.7296 | 331.2242 | 337.8487 | 344.6057 | 351.4978 | 358.5278 | 365.6983
14 |  |  | Network Opex |  |  | 6069 | 6356.64 | 6483.7728 | 6613.4483 | 6745.7172 | 6880.6316 | 7018.2442 | 7158.6091 | 7301.7813 | 7447.8169 | 7596.7732
15 |  |  |  | System operations and network support |  | 4721 | 4254 | 4339 | 4426 | 4515 | 4605 | 4697 | 4791 | 4887 | 4985 | 5084
16 |  |  |  | Business support |  | 9367 | 8172 | 8306 | 9437 | 10071 | 10208 | 10347 | 10489 | 10634 | 10782 | 10998
17 |  |  | Non-network opex |  |  | 14088 | 12426 | 12645 | 13863 | 14586 | 14813 | 15044 | 15280 | 15521 | 15767 | 16082
18 |  |  | Operational expenditure |  |  | 20157 | 18782.64 | 19128.7728 | 20476.4483 | 21331.7172 | 21693.6316 | 22062.2442 | 22438.6091 | 22822.7813 | 23214.8169 | 23678.7732
19 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
20 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
21 | [5 empty] | 2020-03-31: $000 (in constant prices)
22 |  |  |  | Service interruptions and emergencies |  | 1785 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100 | 2100
23 |  |  |  | Vegetation management |  | 816 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832 | 832
24 |  |  |  | Routine and corrective maintenance and inspection |  | 2754 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000 | 3000
25 |  |  |  | Asset replacement and renewal |  | 714 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300 | 300
26 |  |  | Network Opex |  |  | 6069 | 6232 | 6232 | 6232 | 6232 | 6232 | 6232 | 6232 | 6232 | 6232 | 6232
27 |  |  |  | System operations and network support |  | 4721 | 4170.5882 | 4170.5113 | 4170.7187 | 4171.1621 | 4170.8904 | 4170.8016 | 4170.8538 | 4171.0074 | 4171.225 | 4170.6508
28 |  |  |  | Business support |  | 9367 | 8011.7647 | 7983.4679 | 8892.6959 | 9304.0473 | 9245.7001 | 9187.8399 | 9131.3057 | 9076.0166 | 9021.8953 | 9022.1906
29 |  |  | Non-network opex |  |  | 14088 | 12182.3529 | 12153.9792 | 13063.4145 | 13475.2094 | 13416.5905 | 13358.6415 | 13302.1595 | 13247.0241 | 13193.1203 | 13192.8414
30 |  |  | Operational expenditure |  |  | 20157 | 18414.3529 | 18385.9792 | 19295.4145 | 19707.2094 | 19648.5905 | 19590.6415 | 19534.1595 | 19479.0241 | 19425.1203 | 19424.8414
31 |  | Subcomponents of operational expenditure (where known)
32 |  |  |  | Energy efficiency and demand side management, reduction of energy losses
33
34 |  |  |  | Direct billing*
35 |  |  |  | Research and Development
36 |  |  |  | Insurance |  | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249 | 249
37 | * Direct billing expenditure by suppliers that direct bill the majority of their consumers
38
39 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5 | CY+6 | CY+7 | CY+8 | CY+9 | CY+10
40 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31 | 2026-03-31 | 2027-03-31 | 2028-03-31 | 2029-03-31 | 2030-03-31
41 |  | Difference between nominal and real forecasts |  |  |  | 2020-03-31: $000
42 |  |  |  | Service interruptions and emergencies |  | 0 | 42 | 84.84 | 128.5368 | 173.1075 | 218.5697 | 264.9411 | 312.2399 | 360.4847 | 409.6944 | 459.8883
43 |  |  |  | Vegetation management |  | 0 | 16.64 | 33.6128 | 50.9251 | 68.5836 | 86.5952 | 104.9671 | 123.7065 | 142.8206 | 162.317 | 182.2034
44 |  |  |  | Routine and corrective maintenance and inspection |  | 0 | 60 | 121.2 | 183.624 | 247.2965 | 312.2424 | 378.4873 | 446.057 | 514.9781 | 585.2777 | 656.9833
45 |  |  |  | Asset replacement and renewal |  | 0 | 6 | 12.12 | 18.3624 | 24.7296 | 31.2242 | 37.8487 | 44.6057 | 51.4978 | 58.5278 | 65.6983
46 |  |  | Network Opex |  |  | 0 | 124.64 | 251.7728 | 381.4483 | 513.7172 | 648.6316 | 786.2442 | 926.6091 | 1069.7813 | 1215.8169 | 1364.7732
47 |  |  |  | System operations and network support |  | 0 | 83.4118 | 168.4887 | 255.2813 | 343.8379 | 434.1096 | 526.1984 | 620.1462 | 715.9926 | 813.775 | 913.3492
48 |  |  |  | Business support |  | 0 | 160.2353 | 322.5321 | 544.3041 | 766.9527 | 962.2999 | 1159.1601 | 1357.6943 | 1557.9834 | 1760.1047 | 1975.8094
49 |  |  | Non-network opex |  |  | 0 | 243.6471 | 491.0208 | 799.5855 | 1110.7906 | 1396.4095 | 1685.3585 | 1977.8405 | 2273.9759 | 2573.8797 | 2889.1586
50 |  |  | Operational expenditure |  |  | 0 | 368.2871 | 742.7936 | 1181.0337 | 1624.5078 | 2045.0411 | 2471.6027 | 2904.4496 | 3343.7572 | 3789.6966 | 4253.9319

## S12a.Asset Condition
[8 empty] | Company Name | Alpine Energy Limited
[8 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
SCHEDULE 12a: REPORT ON ASSET CONDITION
This schedule requires a breakdown of asset condition by asset class as at the start of the forecast year. The data accuracy assessment relates to the percentage values disclosed in the asset condition columns. Also required is a forecast of the percentage of units to be replaced in the next 5 years. All information should be consistent with the information provided in the AMP and the expenditure on assets forecast in Schedule 11a. All units relating to cable and line assets, that are expressed in km, refer to circuit lengths.
sch ref
7 |  |  |  |  | Asset condition at start of planning period (percentage of units by grade)
8 | [11 empty] | % of asset forecast to be replaced in next 5 years
9 | Voltage | Asset category | Asset class | Units | H1 | H2 | H3 | H4 | H5 | Grade unknown | Data accuracy (1–4)
10 | All | Overhead Line | Concrete poles / steel structure | No. |  |  | 28.62% | 38.53% | 32.85% |  | 3 | 0%
11 | All | Overhead Line | Wood poles | No. | 16.71% | 12.84% | 23.13% | 16.78% | 22.84% | 7.7% | 3 | 6%
12 | All | Overhead Line | Other pole types | No.
13 | HV | Subtransmission Line | Subtransmission OH up to 66kV conductor | km | 0% | 2.15% | 32.41% | 26.59% | 38.85% | 0% | 3 | 0%
14 | HV | Subtransmission Line | Subtransmission OH 110kV+ conductor | km
15 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (XLPE) | km | 0% | 0% | 0% | 13% | 87% | 0% | 4 | 0%
16 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Oil pressurised) | km
17 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (Gas pressurised) | km
18 | HV | Subtransmission Cable | Subtransmission UG up to 66kV (PILC) | km
19 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (XLPE) | km
20 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Oil pressurised) | km
21 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (Gas Pressurised) | km
22 | HV | Subtransmission Cable | Subtransmission UG 110kV+ (PILC) | km
23 | HV | Subtransmission Cable | Subtransmission submarine cable | km
24 | HV | Zone substation Buildings | Zone substations up to 66kV | No. | 4% | 0% | 32% | 0% | 64% |  | 4 | 4%
25 | HV | Zone substation Buildings | Zone substations 110kV+ | No.
26 | HV | Zone substation switchgear | 22/33kV CB (Indoor) | No. |  |  |  |  | 100% |  | 4 | 0%
27 | HV | Zone substation switchgear | 22/33kV CB (Outdoor) | No. | 7.69% | 11.54% | 0% | 19.23% | 61.54% |  | 3 | 7.69%
28 | HV | Zone substation switchgear | 33kV Switch (Ground Mounted) | No. | 0% | 0% | 0% | 0% | 100% | 0% | 4 | 0%
29 | HV | Zone substation switchgear | 33kV Switch (Pole Mounted) | No. | 18.1% | 12.07% | 6.9% | 11.21% | 51.72% | 0% | 3 | 5%
30 | HV | Zone substation switchgear | 33kV RMU | No.
31 | HV | Zone substation switchgear | 50/66/110kV CB (Indoor) | No.
32 | HV | Zone substation switchgear | 50/66/110kV CB (Outdoor) | No. |  |  |  |  | 100% |  | 4 | 0%
33 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (ground mounted) | No. | 5.23% | 0% | 5.23% | 18.61% | 70.93% | 0% | 4 | 4.88%
34 | HV | Zone substation switchgear | 3.3/6.6/11/22kV CB (pole mounted) | No. |  |  |  | 50% | 50% |  | 3 | 0%
35
36 |  |  |  |  | Asset condition at start of planning period (percentage of units by grade)
37 | [11 empty] | % of asset forecast to be replaced in next 5 years
38 | Voltage | Asset category | Asset class | Units | H1 | H2 | H3 | H4 | H5 | Grade unknown | Data accuracy (1–4)
39 | HV | Zone Substation Transformer | Zone Substation Transformers | No. |  | 3.45% | 24.14% | 17.24% | 55.17% |  | 4 | 7.4%
40 | HV | Distribution Line | Distribution OH Open Wire Conductor | km | 0.1% | 32.8% | 23.4% | 14.3% | 29.4% | 0% | 3 | 1%
41 | HV | Distribution Line | Distribution OH Aerial Cable Conductor | km
42 | HV | Distribution Line | SWER conductor | km |  | 100% |  |  |  |  | 3 | 0%
43 | HV | Distribution Cable | Distribution UG XLPE or PVC | km | 0.3% | 0.3% | 3.6% | 5.2% | 90.6% | 0% | 3 | 0.5%
44 | HV | Distribution Cable | Distribution UG PILC | km | 0% | 0% | 0% | 73% | 27% | 0% | 3 | 0%
45 | HV | Distribution Cable | Distribution Submarine Cable | km
46 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (pole mounted) - reclosers and sectionalisers | No. | 1.72% | 0% | 6.9% | 37.93% | 53.45% | 0% | 3 | 1.72%
47 | HV | Distribution switchgear | 3.3/6.6/11/22kV CB (Indoor) | No.
48 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switches and fuses (pole mounted) | No. | 18.77% | 6.09% | 6.03% | 19.02% | 50.09% | 0% | 2 | 6%
49 | HV | Distribution switchgear | 3.3/6.6/11/22kV Switch (ground mounted) - except RMU | No. | 0% | 0% | 10% | 15% | 75% | 0% | 3 | 0%
50 | HV | Distribution switchgear | 3.3/6.6/11/22kV RMU | No. | 2.87% | 21.05% | 26.32% | 14.59% | 35.17% | 0% | 3 | 5%
51 | HV | Distribution Transformer | Pole Mounted Transformer | No. | 1.31% | 31.4% | 23.22% | 26.2% | 17.87% | 0% | 3 | 1.31%
52 | HV | Distribution Transformer | Ground Mounted Transformer | No. | 1.17% | 13.81% | 20.04% | 37.18% | 27.8% | 0% | 3 | 1.25%
53 | HV | Distribution Transformer | Voltage regulators | No. |  |  | 0% | 26.87% | 73.13% |  | 4 | 0%
54 | HV | Distribution Substations | Ground Mounted Substation Housing | No.
55 | LV | LV Line | LV OH Conductor | km | 0.1% | 4% | 54.5% | 34.1% | 7.3% | 0% | 2 | 1%
56 | LV | LV Cable | LV UG Cable | km | 0.09% | 2.15% | 21.15% | 47.37% | 29.24% | 0% | 2 | 1%
57 | LV | LV Streetlighting | LV OH/UG Streetlight circuit | km
58 | LV | Connections | OH/UG consumer service connections | No.
59 | All | Protection | Protection relays (electromechanical, solid state and numeric) | No. | 4.72% | 0% | 6.88% | 59.33% | 29.07% |  | 4 | 4%
60 | All | SCADA and communications | SCADA and communications equipment operating as a single system | Lot | 0% | 9% | 1% | 11% | 79% |  | 2
61 | All | Capacitor Banks | Capacitors including controls | No. | 0% | 5.89% | 11.76% | 23.53% | 58.82% |  | 3 | 6%
62 | All | Load Control | Centralised plant | Lot | 8% | 0% | 17% | 25% | 50% |  | 3 | 8%
63 | All | Load Control | Relays | No. | 4% |  |  | 20% | 76% |  | 2
64 | All | Civils | Cable Tunnels | km |  |  |  |  | 100% |  | 4 | 0%

## S12b.Capacity Forecast
[10 empty] | Company Name | Alpine Energy Limited
[10 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
SCHEDULE 12b: REPORT ON FORECAST CAPACITY
This schedule requires a breakdown of current and forecast capacity and utilisation for each zone substation and current distribution transformer capacity. The data provided should be consistent with the information provided in the AMP. Information provided in this table should relate to the operation of the network in its normal steady state configuration.
sch ref
7 | 12b(i): System Growth - Zone Substations
8 |  | Existing Zone Substations | Current Peak Load (MVA) | Installed Firm Capacity (MVA) | Security of Supply Classification (type) | Transfer Capacity (MVA) | Utilisation of Installed Firm Capacity % | Installed Firm Capacity +5 years (MVA) | Utilisation of Installed Firm Capacity + 5yrs % | Installed Firm Capacity Constraint +5 years (cause) | Explanation
9 |  | Albury (ABY) | 4.5531 | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
10 |  | Balmoral (BML) | #N/A | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
11 |  | Bells Pond (BPD) | 15.6306 | 20 | N-1 | 0 | 78.15% | 20 | 1.2745 | Transformer | T1 installed FY18/19, T2 to be upgraded to relieve constraint
12 |  | Clandeboye 1 (CD1) | 14.1809 | 20 | N-1 | 0 | 70.9% | 30 | 0.64521 | Transformer | Upgrade transformers to relieve constraint
13 |  | Clandeboye 2 (CD2) | 18.8472 | 25 | N-1 | 0 | 75.39% | 25 | 0.87541 | No constraint within +5 years | Meets Alpine Security standard due to sufficient 11 kV backup
14 |  | Cooney's Road (CNR) | 4.14 | 0 | N | 1.8/0.8/0.6* | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
15 |  | Fairlie (FLE) | 2.83 | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
16 |  | Geraldine (GLD) | 6.396 | 0 | N | 0 | - | 7.5 | 0.94974 | No constraint within +5 years | Options being assessed to upgrade installed firm capacity
17 |  | Haldon Lilybank (HLB) | 0.51764 | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
18 |  | Pareora (PAR) | 10.31 | 15 | N-1 | 0 | 68.73% | 15 | 0.74194 | No constraint within +5 years | Meets Alpine security standard
19 |  | Pleasant Point (PLP) | 4.997 | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
20 |  | Rangitata (RGA) | 10.4107 | 10 | N-1 | 0 | 104.1% | 10 | 1.0965 | Subtransmission circuit | Line capacity constraint, sufficient 11 kV backup in place
21 |  | Studholme (STU) | 14.118 | 10 | N-1 | 0 | 141.2% | 10 | 1.9085 | Transpower | Transpower two 11 MVA transformers, load shedding/shift required
22 |  | Tekapo Village (TEK) | 3.9511 | 0 | N | 0 | - | 15 | 0.71514 | Subtransmission circuit | Options being assessed to upgrade installed firm capacity
23 |  | Temuka (TMK) | 13.7134 | 25 | N-1 | 0 | 54.85% | 25 | 0.57776 | No constraint within +5 years | Meets Alpine Security standard
24 |  | Timaru 11/33 kV (TIM) | 17.3744 | 25 | N-1 Switched | 0 | 69.5% | 25 | 0.75019 | No constraint within +5 years | Meets Alpine Security standard
25 |  | Twizel Village (TVS) | 3.9176 | 0 | N | 0 | - | 6.25 | 0.8042 | No constraint within +5 years | Options being assessed to upgrade installed firm capacity
26 |  | Unwin Hut (UHT) | 0.99398 | 0 | N | 0 | - | 0 | - | No constraint within +5 years | Meets Alpine security standard
27 |  | [Zone Substation_19] |  |  |  |  | - |  |  | [Select one]
28 |  | [Zone Substation_20] |  |  |  |  | - |  |  | [Select one]
29 |  | ¹ Extend forecast capacity table as necessary to disclose all capacity by each zone substation

## S12c.Demand Forecast
[8 empty] | Company Name | Alpine Energy Limited
[8 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
SCHEDULE 12C: REPORT ON FORECAST NETWORK DEMAND
This schedule requires a forecast of new connections (by consumer type), peak demand and energy volumes for the disclosure year and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumptions used in developing the expenditure forecasts in Schedule 11a and Schedule 11b and the capacity and utilisation forecasts in Schedule 12b.
sch ref
7 | 12c(i): Consumer Connections
8 |  |  | Number of ICPs connected in year by consumer type |  |  | Number of connections
9 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
10 |  |  |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
11 |  |  |  | Consumer types defined by EDB*
12 |  |  |  | Low Charge |  | 11249.1348 | 11351.187 | 11454.1651 | 11558.0774 | 11662.9324 | 11768.7386
13 |  |  |  | Low Uncontrolled |  | 45.4082 | 45.8202 | 46.2359 | 46.6553 | 47.0786 | 47.5057
14 |  |  |  | 015 |  | 18996.7896 | 19169.1287 | 19343.0312 | 19518.5114 | 19695.5835 | 19874.262
15 |  |  |  | 015 Uncontrolled |  | 76.1849 | 76.8761 | 77.5735 | 78.2773 | 78.9874 | 79.704
16 |  |  |  | 360 |  | 1258.8173 | 1270.2373 | 1281.7609 | 1293.3891 | 1305.1227 | 1316.9628
17 |  |  |  | 360 Uncontrolled |  | 29.2631 | 29.5286 | 29.7964 | 30.0668 | 30.3395 | 30.6148
18 |  |  |  | Assessed |  | 1693.7274 | 1709.0929 | 1724.5978 | 1740.2434 | 1756.0309 | 1771.9616
19 |  |  |  | TOU 400V |  | 141.2701 | 142.5517 | 143.8449 | 145.1499 | 146.4667 | 147.7954
20 |  |  |  | TOU 11kV |  | 10.0907 | 10.1823 | 10.2746 | 10.3678 | 10.4619 | 10.5568
21 |  |  |  | IND |  | 12.1089 | 12.2187 | 12.3296 | 12.4414 | 12.5543 | 12.6682
22 |  |  | Connections total |  |  | 33512.795 | 33816.8234 | 34123.61 | 34433.1797 | 34745.5578 | 35060.7698
23 |  |  |  | *include additional rows if needed
24 |  | Distributed generation
25 |  |  |  | Number of connections |  | 428.3 | 493.5 | 558.7 | 623.9 | 689.1 | 754.3
26 |  |  |  | Capacity of distributed generation installed in year (MVA) |  | 1.9961 | 2.3 | 2.6039 | 2.9078 | 3.2116 | 3.5155
27 | 12c(ii) System Demand
28 | [5 empty] | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
29 |  | Maximum coincident system demand (MW) |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
30 |  |  |  | GXP demand |  | 140.0858 | 142.6227 | 145.2055 | 147.8352 | 150.5124 | 153.2381
31 |  | plus |  | Distributed generation output at HV and above |  | 2.3722 | 2.4152 | 2.4589 | 2.5034 | 2.5488 | 2.5949
32 |  |  | Maximum coincident system demand |  |  | 142.458 | 145.0378 | 147.6644 | 150.3386 | 153.0612 | 155.8331
33 |  | less |  | Net transfers to (from) other EDBs at HV and above |  | 0
34 |  |  | Demand on system for supply to consumers' connection points |  |  | 142.458 | 145.0378 | 147.6644 | 150.3386 | 153.0612 | 155.8331
35 |  | Electricity volumes carried (GWh)
36 |  |  |  | Electricity supplied from GXPs |  | 819.6996 | 834.5441 | 849.6574 | 865.0444 | 880.7101 | 896.6595
37 |  | less |  | Electricity exports to GXPs |  | 16.7712 | 17.0749 | 17.3841 | 17.6989 | 18.0194 | 18.3458
38 |  | plus |  | Electricity supplied from distributed generation |  | 29.1864 | 29.7149 | 30.2531 | 30.8009 | 31.3587 | 31.9266
39 |  | less |  | Net electricity supplied to (from) other EDBs |  | 0 | 0 | 0 | 0 | 0 | 0
40 |  |  | Electricity entering system for supply to ICPs |  |  | 832.1148 | 847.1842 | 862.5264 | 878.1465 | 894.0494 | 910.2404
41 |  | less |  | Total energy delivered to ICPs |  | 809.0759 | 823.7281 | 838.6455 | 853.8331 | 869.2958 | 885.0384
42 |  |  | Losses |  |  | 23.0389 | 23.4561 | 23.8809 | 24.3134 | 24.7537 | 25.202
43
44 |  |  | Load factor |  |  | 66.68% | 66.68% | 66.68% | 66.68% | 66.68% | 66.68%
45 |  |  | Loss ratio |  |  | 2.769% | 2.769% | 2.769% | 2.769% | 2.769% | 2.769%

## S12d.Reliability Forecast
[6 empty] | Company Name | Alpine Energy Limited
[6 empty] | AMP Planning Period | 1 April 2020 – 31 March 2030
Network / Sub-network Name
SCHEDULE 12d: REPORT FORECAST INTERRUPTIONS AND DURATION
This schedule requires a forecast of SAIFI and SAIDI for disclosure and a 5 year planning period. The forecasts should be consistent with the supporting information set out in the AMP as well as the assumed impact of planned and unplanned SAIFI and SAIDI on the expenditures forecast provided in Schedule 11a and Schedule 11b.
sch ref
8 |  |  |  | Current Year CY | CY+1 | CY+2 | CY+3 | CY+4 | CY+5
9 |  |  | for year ended | 2020-03-31 | 2021-03-31 | 2022-03-31 | 2023-03-31 | 2024-03-31 | 2025-03-31
10 | SAIDI
11 |  | Class B (planned interruptions on the network) |  | 27.96 | 54.99 | 54.99 | 54.99 | 54.99 | 54.99
12 |  | Class C (unplanned interruptions on the network) |  | 95.23 | 91.88 | 91.88 | 91.88 | 91.88 | 91.88
13 | SAIFI
14 |  | Class B (planned interruptions on the network) |  | 0.2 | 0.6986 | 0.6986 | 0.6986 | 0.6986 | 0.6986
15 |  | Class C (unplanned interruptions on the network) |  | 0.73 | 1.197 | 1.197 | 1.197 | 1.197 | 1.197